## Approved Pre-Rinse Sprayers (hidden)
Labeled Product: Product Brand Name | Model Name | Model Number | Maximum Flow Rate (gallons per minute) | Spray Force (ounces-force)
Fisher |  | 10197 | 0.7 | 4.2
Fisher |  | 10227 | 0.7 | 4.2
Fisher |  | 13641 | 0.7 | 4.2
Fisher |  | 13692 | 0.7 | 4.2
T&S Brass |  | B-0107-C | 0.65 | 4.4
T&S Brass |  | EB-0107-C | 0.65 | 4.4
Encore Series | Retro-fit Spray valve and Grip | KLP50-0220-65 | 0.67 | 4.5
Encore Series | Pre-rinse Spray Valve Assembly | KLP50-Y002-65 | 0.67 | 4.5
T&S Brass |  | B-0108-C | 0.65 | 4.6
Encore Series | Retro-fit Spray Valve and Grip | KLP50-0220-74 | 0.74 | 4.9
Encore Series | Pre-rinse Spray Valve Assembly | KLP50-Y002-74 | 0.74 | 4.9
Chicago Faucet |  | 90-LABCP | 1 | 6.4
Chicago Faucet |  | 90-LMPABCP | 1 | 6.4
Chicago Faucet |  | 90-ANGABCP | 1 | 6.4
Encore Series | Retro-fit Spray Valve and Grip | KLP50-0220105 | 1.05 | 6.8
Encore Series | Pre-rinse Spray Valve Assembly | KLP50-Y002105 | 1.05 | 6.8
T&S Brass |  | B-0107-J | 1.07 | 7.2
T&S Brass |  | EB-0107-J | 1.07 | 7.2
Encore Series | Pre-rinse Spray Valve Assembly | KLP50-Y002-12 | 1.22 | 7.3
Encore Series | Retro-fit Spray Valve and Grip | KLP50-0220-12 | 1.22 | 7.3
Kason | 8" Wall Mount Pre-Rinse Unit, WaterSense | 0451KL8500WS | 1.2 | 7.4
Kason | Double Pantry Deck Mount Pre-Rinse Unit, WaterSense | 0452KL1500WS | 1.2 | 7.4
Kason | Sgl Pantry Deck Mount Pre-Rinse Unit, WaterSense | 0452KL2500WS | 1.2 | 7.4
Kason | 4" Deck Mount Pre-Rinse Unit, WaterSense | 0452KL4500WS | 1.2 | 7.4
Kason | 8" Deck Mount Pre-Rinse Unit, WaterSense | 0452KL8500WS | 1.2 | 7.4
Fisher |  | 71307 | 1.15 | 7.5
Fisher |  | 64548 | 1.15 | 7.5
Fisher |  | 2949 | 1.15 | 7.5
Fisher |  | 2949R | 1.15 | 7.5
T&S Brass |  | 5SV-C | 1.2 | 7.7
equal to minimum federal standards - would not qualify
exceeds federal standards - should be removed from list

## Summary
Energize Delaware
Energy Efficiency Investment Fund (EEIF) for Non-Profits |  |  |  | Version 7.3 - 2025
Prescriptive HVAC/Heating Grant Application Calculator - Project Summary
[7 empty] | Measure Name | Savings |  |  | Estimated Incentive ($)
[8 empty] | kW | kWh | MMBtu
Project Info (Required) |  | Energy Savings Summary |  |  |  |  | Air Conditioners | 0 | 0 | - | 0
Building Type (Select from list):* |  | Estimated Peak Demand Savings (kW) | Estimated Annual Energy Savings (kWh) | Annual Fossil Fuel Savings (MMBtu) | Annual Gas Savings (Therms) | Annual GHG Savings (TonCO2) | Air Source Heat Pumps | 0 | 0 | - | 0
Zip Code | [6 empty] | Ductless Mini-Splits | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | PTACs & PTHPs | 0 | 0 | - | 0
Project Costs | [6 empty] | Chillers | 0 | 0 | - | 0
Estimated Materials Cost | [6 empty] | Gas Furnaces | - | - | 0 | 0
Estimated Labor Costs | [6 empty] | Condensing Unit Heaters | - | - | 0 | 0
Estimated Additional Costs |  | Estimated Incentive | 0 |  |  |  | Infrared Heaters | - | - | 0 | 0
Estimated Total Project Cost | 0 | % towards Cost Cap |  |  |  |  | Gas Boilers | - | - | 0 | 0
Note: All cost values should match quote/estimate provided | [6 empty] | Tankless Water Heaters | - | - | 0 | 0
[7 empty] | Heat Pump Water Heater | 0 | 0 | 0 | 0
[7 empty] | High Efficiency Indirect WHs | - | - | 0 | 0
[7 empty] | Condensing Stand-Alone WHs | - | - | 0 | 0
[7 empty] | Boiler Controls | - | - | 0 | 0
[7 empty] | Steam Traps | - | - | 0 | 0
[7 empty] | Smart Thermostats | - | 0 | 0 | 0
[7 empty] | HVAC VFDs | 0 | 0 | - | 0
**Calculator file originally developed by NV5 for the DNREC EEIF Program** | [6 empty] | AC Tune-Up | 0 | 0 | - | 0
[7 empty] | Dual Enthalpy Economizers | 0 | 0 | - | 0
Contact Information: - For inquiries regarding the EEIF for Non-Profits program and application process, please contact Energize Delaware's representative ICF at 888-735-1510 or email aeg-energizede@icf.com - For questions about the DNREC EEIF program and/or business inquiries, please email DNREC.EnergyPrograms@delaware.gov - For DNREC EEIF application assistance, please email DCCE.EnergyRebates@NV5.com | [6 empty] | Evaporator Fan ECM Retrofit | 0 | 0 | - | 0
[7 empty] | Screw Air Compressor VSD | 0 | 0 | - | 0
[7 empty] | Total | 0 | 0 | 0 | 0
QA Reviewer & Date
QC Reviewer & Date

## Calculator Instructions
Energize Delaware Energy Efficiency Investment Fund (EEIF) for Non-Profits Calculator for Prescriptive HVAC/Heating Measures
***This calculator is used for estimating savings and incentives from the installation of prescriptive HVAC measures. The measure inputs used in this calculator by an applicant will be reviewed by the Program in order to determine the final incentive amount. The Program reserves the right to inspect any and all measures prior to any incentive payment.
For inquiries regarding the EEIF for Non-Profits program and application process, please contact Energize Delaware's representative ICF at 888-735-1510 or email aeg-energizede@icf.com
Input Instructions
Use the color-coded reference cells. Only yellow cells need input.
Requires Input
Doesn't Need an Input
Output Cell
In order to begin using the calculator, the Applicant Information page must be filled out. Zip code (Row 8) and the building type (Row 35) are required to populate incentives.
1 MBH = 1,000 Btu/h
1 MMBtu = 1,000,000 Btu/h
Resources
AHRI Directory: | https://www.ahridirectory.org/Search/SearchHome?ReturnUrl=%2f
Energy Star Product Finder: | https://www.energystar.gov/productfinder/
Mid-Atlantic TRM V9: | https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf
Delaware 2021 TRM

## Incentive Levels
Delaware Energy Efficiency Investment Fund
Prescriptive HVAC/Heating Grant Application
Division of Climate, Coastal, & Energy | [6 empty] | Version 7.3 - 2025
100 W. Water Street, Suite 10B, Dover, DE 19904 Phone: (302) 735 – 3480
Prescriptive Heating Incentive Levels
Terms Explained
ECM: Electronic Commutated Motor |  | EF: Energy Factor |  |  |  | AFUE: Annual Fuel Utilization Efficiency
Air Conditioning Equipment
Description |  | Specification |  |  | Incentive per unit |  |  | Unit
Air Conditioners |  | AHRI Certified, meets efficiency requirements from tables below |  |  | 250 |  |  | Tons
Air Source Heat Pumps |  | AHRI Certified, meets efficiency requirements from tables below |  |  | 1000 |  |  | Tons
Ductless Mini-Split Heat Pumps |  | AHRI Certified, meets efficiency requirements from tables below |  |  | 1250 |  |  | Tons
VRF Ductless Heat Pumps |  | AHRI Certified, meets efficiency requirements from tables below |  |  | 1500 |  |  | Tons
Packaged Terminal Air Conditioner |  | AHRI Certified, meets efficiency requirements from tables below |  |  | 100 |  |  | Tons
Packaged Terminal Heat Pump |  | AHRI Certified, meets efficiency requirements from tables below |  |  | 250 |  |  | Tons
Chillers |  | AHRI Certified, meets efficiency requirements from tables below |  |  | 50 |  |  | Tons
|  | Performance Incentive for each 0.01 kW/ton point below qualifying efficiency relative to IPLV |  |  | 5 |  |  | kW/Ton
Natural Gas Heating Equipment
Description |  | Specification |  |  | Incentive per unit |  |  | Unit
Furnace up to 150 MBH |  | 95% AFUE or greater with ECM |  |  | 750 |  |  | Each
Furnace up to 150 MBH |  | 97% AFUE or greater with ECM |  |  | 1000 |  |  | Each
Condensing Unit Heater up to 300 MBH |  | 90% or greater thermal efficiency |  |  | 750 |  |  | Each
Infrared Heater, all sizes |  | Low Intensity |  |  | 750 |  |  | Each
Condensing Boiler up to 300 MBH |  | 90% AFUE or greater |  |  | 1000 |  |  | Each
Condensing Boiler up to 300 MBH |  | 95% AFUE or greater |  |  | 1500 |  |  | Each
Water Heating Equipment
Description |  | Specification |  |  | Incentive per unit |  |  | Unit
On-Demand Tankless with electronic ignition |  | EF of 0.82 or greater |  |  | 750 |  |  | Each
On-Demand Tankless with electronic ignition |  | EF of 0.95 or greater |  |  | 1000 |  |  | Each
Commercial Heat Pump Water Heater |  | UEF 3.0+ |  |  | 750 |  |  | Each
|  | UEF 3.3+ |  |  | 1000 |  |  | Each
High Efficiency Indirect Water Heater |  | EF of ≥0.82 OR combined appliance efficiency rating of ≥85% |  |  | 400 |  |  | Each
Condensing Stand Alone 75 to 300 MBH |  | 95% or greater thermal efficiency |  |  | 1000 |  |  | Each
Miscellaneous
Description |  | Specification |  |  | Incentive per unit |  |  | Unit
Air Compressor VSD |  | Constant Speed compressor to VSD |  |  | 200 |  |  | HP
After Market Boiler Reset Controls |  |  |  |  | 225 |  |  | Each
Steam Traps |  | more than 70 per project requires pre-approval |  |  | 50 |  |  | Each
Smart Thermostats |  | Heating and cooling systems <65,000 Btu/h |  |  | 100 |  |  | Each
VFDs on HVAC (Supply/Return/Exhaust Fans, CHW Pumps, HHW Pumps ONLY) |  | For HVAC Motors <5 HP, without a VFD currently installed |  |  | 50 |  |  | HP
|  | For HVAC Motors 5-10 HP, without a VFD currently installed |  |  | 75 |  |  | HP
|  | For HVAC Motors 10 - 200 HP, without a VFD currently installed |  |  | 100 |  |  | HP
AC Tune Up < 65,000 BTUh |  |  |  |  | 50 |  |  | Each
Dual Enthalpy Economizer |  |  |  |  | 150 |  |  | Ton
ECM Evap Fan Motor |  | Synchronous motor - case cooler |  |  | 60 |  |  | Each
|  | Synchronous motor - walk-in cooler |  |  | 100 |  |  | Each
Air Cooled Air Conditioners
| Size Category | Heating Type | Qualifying Efficiency
| <5.4 tons Split | Any | (Prior to 1/1/2023) 15.0 SEER & 12.5 EER OR (After 1/1/2023) 15.2 SEER2 & 12 EER2
| <5.4 tons Packaged | Any | (Prior to 1/1/2023) 15.0 SEER & 12.5 EER OR (After to 1/1/2023) 15.2 SEER2 & 11.5 EER2
| ≥5.4 to <11.25 tons | Electric Resistance (or None) | 12.2 EER & 14.0 SEER
|  | Other | 12 EER & 13.8 IEER/SEER
| ≥11.25 to <20 tons | Electric Resistance (or None) | 12.2 EER & 13.2 IEER/SEER
|  | Other | 12 EER & 13 IEER/SEER
| ≥20 to <63.3 tons | Electric Resistance (or None) | 10.5 EER & 12.3 IEER/SEER
|  | Other | 10.3 EER & 12.1 IEER/SEER
| ≥63.3 tons | Electric Resistance (or None) | 9.9 EER & 11.6 IEER/SEER
|  | Other | 9.7 EER & 11.4 IEER/SEER
Water Cooled Air Conditioners
| Size Category | Heating Type | Qualifying Efficiency
| <5.4 tons | Electric Resistance (or None) | 14.0 EER
|  | Other | 14.0 EER
| ≥5.4 to <11.25 tons | Electric Resistance (or None) | 14.0 EER & 15.3 IEER/SEER
|  | Other | 13.8 EER & 15.1 IEER/SEER
| ≥11.25 to <20 tons | Electric Resistance (or None) | 14.0 EER & 14.8 IEER/SEER
|  | Other | 13.8 EER & 14.6 IEER/SEER
| ≥20 to <63.3 tons | Electric Resistance (or None) | 14.0 EER & 14.8 IEER/SEER
|  | Other | 13.8 EER & 14.6 IEER/SEER
| ≥63.3 tons | Electric Resistance (or None) | 14.0 EER & 14.8 IEER/SEER
|  | Other | 13.8 EER & 14.6 IEER/SEER
Evaporatively Cooled Air Conditioners
| Size Category | Heating Type | Qualifying Efficiency
| <5.4 tons | Electric Resistance (or None) | 14.0 EER
|  | Other | 14.0 EER
| ≥5.4 to <11.25 tons | Electric Resistance (or None) | 14.0 EER & 15.3 IEER/SEER
|  | Other | 13.8 EER & 15.1 IEER/SEER
| ≥11.25 to <20 tons | Electric Resistance (or None) | 13.5 EER & 14.3 IEER/SEER
|  | Other | 13.3 EER & 14.1 IEER/SEER
| ≥20 to <63.3 tons | Electric Resistance (or None) | 13.5 EER & 14.3 IEER/SEER
|  | Other | 13.3 EER & 14.1 IEER/SEER
| ≥63.3 tons | Electric Resistance (or None) | 13.5 EER & 14.3 IEER/SEER
|  | Other | 13.3 EER & 14.1 IEER/SEER
Air Source Heat Pumps
| Size Category | Heating Type | Qualifying Efficiency
| <5.4 tons Split | Any | (Prior to 1/1/2023) 16.0 SEER 11.5 EER 9 HSPF OR (After to 1/1/2023) 16 SEER2 11.0 EER2 8.0 HSPF2
| <5.4 tons Packaged | Any | (Prior to 1/1/2023) 16.0 SEER 10.4 EER 8.8 HSPF OR (After to 1/1/2023) 15.2 SEER2 10.0 EER2 7.2 HSPF2
| ≥5.4 to <11.25 tons | Electric Resistance (or None) | 11.8 EER & 13.6 IEER/SEER & 3.4 COP/HSPF
|  | Other | 11.6 EER & 13.4 IEER/SEER & 3.4 COP/HSPF
| ≥11.25 to <20 tons | Electric Resistance (or None) | 10.9 EER & 12.8 IEER/SEER & 3.3 COP/HSPF
|  | Other | 10.7 EER & 12.6 IEER/SEER & 3.3 COP/HSPF
| ≥20 to <63.3 tons | Electric Resistance (or None) | 10.3 EER & 11.8 IEER/SEER & 3.3 COP/HSPF
|  | Other | 10.1 EER & 11.6 IEER/SEER & 3.3 COP/HSPF
Ductless Mini Split Heat Pumps
| Size Category | Heating Type | Qualifying Efficiency
| <5.4 tons | All | 16.0 SEER2 11.0 EER2 8 HSPF2
VRF Ductless Mini Split Heat Pumps
| Size Category | Heating Type | Qualifying Efficiency
| <5.4 tons | All | 16.0 SEER2 11.0 EER2 8 HSPF2
Packaged Terminal Air Conditioners
| Standard Size | Heating Type | Qualifying Efficiency
| < .75 tons | All | 12.81 EER
| > .75 and < 1 ton | All | 11.87 EER
| > 1 ton | All | 10.92 EER
| Non-Standard Size* | Heating Type | Qualifying Efficiency
| < .75 tons | All | 10.1 EER
| > .75 and < 1 ton | All | 9.43 EER
| > 1 ton | All | 8.76 EER
* Replacement unit shall be factory labeled as follows: “MANUFACTURED FOR REPLACEMENT APPLICATIONS ONLY: NOT TO BE INSTALLED IN NEW CONSTRUCTION PROJECTS.” Replacement efficiencies apply only to units with existing sleeves less than 16 inches (406 mm) in height and less than 42 inches (1067 mm) in width
Packaged Terminal Heat Pumps
| Standard Size | Heating Type | Qualifying Efficiency
| < .75 tons | All | 12.81 EER & 3.19 COP
| > .75 and < 1 ton | All | 11.87 EER & 3.12 COP
| > 1 ton | All | 10.92 EER & 3.03 COP
| Non-Standard Size* | Heating Type | Qualifying Efficiency
| < .75 tons | All | 10.0 EER & 2.88 COP
| > .75 and < 1 ton | All | 9.32 EER & 2.80 COP
| > 1 ton | All | 8.65 EER & 2.72 COP
* Replacement unit shall be factory labeled as follows: “MANUFACTURED FOR REPLACEMENT APPLICATIONS ONLY: NOT TO BE INSTALLED IN NEW CONSTRUCTION PROJECTS.” Replacement efficiencies apply only to units with existing sleeves less than 16 inches (406 mm) in height and less than 42 inches (1067 mm) in width
Air-Cooled Chillers
| Size Category | Compliance Path* | Qualifying Efficiency (Must Meet Both)
|  |  | Full Load - EER | IPLV - EER
| <150 Tons | Path A | ≥10.605 | ≥14.385
|  | Path B | ≥10.185 | ≥16.59
| ≥150 tons | Path A | ≥10.605 | ≥14.7
|  | Path B | ≥10.185 | ≥16.905
Water Cooled, Electrically Operated, Positive Displacement Chillers
| Size Category | Compliance Path* | Qualifying Efficiency (Must Meet Both)
|  |  | Full Load kW/Ton | IPLV kW/Ton
| <75 tons | Path A | ≤0.713 | ≤0.57
|  | Path B | ≤0.741 | ≤0.475
| ≥75 and <150 tons | Path A | ≤0.684 | ≤0.532
|  | Path B | ≤0.713 | ≤0.466
| ≥150 and <300 tons | Path A | ≤0.627 | ≤0.513
|  | Path B | ≤0.646 | ≤0.418
| ≥300 tons and <600 tons | Path A | ≤0.58 | ≤0.494
|  | Path B | ≤0.594 | ≤0.39
| ≥600 tons | Path A | ≤0.532 | ≤0.475
|  | Path B | ≤0.556 | ≤0.361
Water Cooled, Electrically Operated, Centrifugal Chillers
| Size Category | Compliance Path* | Qualifying Efficiency (Must Meet Both)
|  |  | Full Load kW/Ton | IPLV kW/Ton
| <150 tons | Path A | ≤0.58 | ≤0.523
|  | Path B | ≤0.66 | ≤0.418
| ≥150 and <300 tons | Path A | ≤0.58 | ≤0.523
|  | Path B | ≤0.603 | ≤0.38
| ≥300 and <400 tons | Path A | ≤0.532 | ≤0.494
|  | Path B | ≤0.565 | ≤0.371
| ≥400 and <600 tons | Path A | ≤0.532 | ≤0.475
|  | Path B | ≤0.556 | ≤0.361
| ≥600 tons | Path A | ≤0.532 | ≤0.475
|  | Path B | ≤0.556 | ≤0.361
*Path A is intended for applications where significant operating time is expected at full-load conditions. Path B is an alternative set of efficiency levels for water-cooled chillers intended for applications where significant time is expected at part load. All Path B chillers are required to be equipped with demand-limiting controls. Compliance with the code can be achieved by meeting the requirements of either Path A or B. However, both full-load and IPLV levels must be met to fulfill the requirements of Path A or B.

## HPWH Efficiency Reqs (hidden)
Measure Case Capacity (gal) | Measure Case Efficiency (UEF) | Base Case Definition | Base Case Efficiency (UEF) | Base Case Equipment Type | Measure Offering Description (text)
> 55 to <=75 | 3.3 | 60 Gal | 0.61 | NG Storage | Heat pump water heater, > 55 to <= 75 gal, UEF = 3.30 replacing storage natural gas water heater, 60 gal, UEF = 0.61
> 55 to <=75 | 3.5 | 60 Gal | 0.61 | NG Storage | Heat pump water heater, > 55 to <= 75 gal, UEF = 3.50 replacing storage natural gas water heater, 60 gal, UEF = 0.61
> 55 to <=75 | 3.75 | 60 Gal | 0.61 | NG Storage | Heat pump water heater, > 55 to <= 75 gal, UEF = 3.75 replacing storage natural gas water heater, 60 gal, UEF = 0.61
> 75 | 3.3 | 75 Gal | 0.59 | NG Storage | Heat pump water heater, > 75 gal, UEF = 3.30 replacing storage natural gas water heater, 75 gal, UEF = 0.59
> 75 | 3.5 | 75 Gal | 0.59 | NG Storage | Heat pump water heater, > 75 gal, UEF = 3.50 replacing storage natural gas water heater, 75 gal, UEF = 0.59
> 75 | 3.75 | 75 Gal | 0.59 | NG Storage | Heat pump water heater, > 75 gal, UEF = 3.75 replacing storage natural gas water heater, 75 gal, UEF = 0.59
>= 45 to <= 55 | 3.3 | 30 Gal | 0.6 | NG Storage | Heat pump water heater, >= 45 to <= 55 gal, UEF = 3.30 replacing storage natural gas water heater, 30 gal, UEF = 0.60
>= 45 to <= 55 | 3.3 | 40 Gal | 0.64 | NG Storage | Heat pump water heater, >= 45 to <= 55 gal, UEF = 3.30 replacing storage natural gas water heater, 40 gal, UEF = 0.64
>= 45 to <= 55 | 3.3 | 50 Gal | 0.63 | NG Storage | Heat pump water heater, >= 45 to <= 55 gal, UEF = 3.30 replacing storage natural gas water heater, 50 gal, UEF = 0.63
>= 45 to <= 55 | 3.3 | High Draw | 0.81 | NG Tankless | Heat pump water heater, >= 45 to <= 55 gal, UEF = 3.30 replacing tankless natural gas water heater, High Draw, UEF = 0.81
>= 45 to <= 55 | 3.5 | 30 Gal | 0.6 | NG Storage | Heat pump water heater, >= 45 to <= 55 gal, UEF = 3.50 replacing storage natural gas water heater, 30 gal, UEF = 0.60
>= 45 to <= 55 | 3.5 | 40 Gal | 0.64 | NG Storage | Heat pump water heater, >= 45 to <= 55 gal, UEF = 3.50 replacing storage natural gas water heater, 40 gal, UEF = 0.64
>= 45 to <= 55 | 3.5 | 50 Gal | 0.63 | NG Storage | Heat pump water heater, >= 45 to <= 55 gal, UEF = 3.50 replacing storage natural gas water heater, 50 gal, UEF = 0.63
>= 45 to <= 55 | 3.5 | High Draw | 0.81 | NG Tankless | Heat pump water heater, >= 45 to <= 55 gal, UEF = 3.50 replacing tankless natural gas water heater, High Draw, UEF = 0.81
>= 45 to <= 55 | 3.75 | 30 Gal | 0.6 | NG Storage | Heat pump water heater, >= 45 to <= 55 gal, UEF = 3.75 replacing storage natural gas water heater, 30 gal, UEF = 0.60
>= 45 to <= 55 | 3.75 | 40 Gal | 0.64 | NG Storage | Heat pump water heater, >= 45 to <= 55 gal, UEF = 3.75 replacing storage natural gas water heater, 40 gal, UEF = 0.64
>= 45 to <= 55 | 3.75 | 50 Gal | 0.63 | NG Storage | Heat pump water heater, >= 45 to <= 55 gal, UEF = 3.75 replacing storage natural gas water heater, 50 gal, UEF = 0.63
>= 45 to <= 55 | 3.75 | High Draw | 0.81 | NG Tankless | Heat pump water heater, >= 45 to <= 55 gal, UEF = 3.75 replacing tankless natural gas water heater, High Draw, UEF = 0.81
> 75 | 3.3 | 75 gal | 3 | Heat pump | Heat pump water heater, > 75 gal, UEF = 3.30, replacing heat pump water heater, 75 gal, UEF = 3.00
> 75 | 3.5 | 75 gal | 3 | Heat pump | Heat pump water heater, > 75 gal, UEF = 3.50, replacing heat pump water heater, 75 gal, UEF = 3.00
> 75 | 3.75 | 75 gal | 3 | Heat pump | Heat pump water heater, > 75 gal, UEF = 3.75, replacing heat pump water heater, 75 gal, UEF = 3.00
>=45 to <=55 | 3.3 | 30 gal | 0.92 | Electric storage | Heat pump water heater, => 45 to <= 55 gal, UEF = 3.30, replacing electric storage water heater, 30 gal, UEF = 0.92
>=45 to <=55 | 3.3 | 40 gal | 0.92 | Electric storage | Heat pump water heater, => 45 to <= 55 gal, UEF = 3.30, replacing electric storage water heater, 40 gal, UEF = 0.92
>=45 to <=55 | 3.3 | 50 gal | 0.92 | Electric storage | Heat pump water heater, => 45 to <= 55 gal, UEF = 3.30, replacing electric storage water heater, 50 gal, UEF = 0.92
>=45 to <=55 | 3.5 | 30 gal | 0.92 | Electric storage | Heat pump water heater, => 45 to <= 55 gal, UEF = 3.50, replacing electric storage water heater, 30 gal, UEF = 0.92
>=45 to <=55 | 3.5 | 40 gal | 0.92 | Electric storage | Heat pump water heater, => 45 to <= 55 gal, UEF = 3.50, replacing electric storage water heater, 40 gal, UEF = 0.92
>=45 to <=55 | 3.5 | 50 gal | 0.92 | Electric storage | Heat pump water heater, => 45 to <= 55 gal, UEF = 3.50, replacing electric storage water heater, 50 gal, UEF = 0.92
>=45 to <=55 | 3.75 | 30 gal | 0.92 | Electric storage | Heat pump water heater, => 45 to <= 55 gal, UEF = 3.75, replacing electric storage water heater, 30 gal, UEF = 0.92
>=45 to <=55 | 3.75 | 40 gal | 0.92 | Electric storage | Heat pump water heater, => 45 to <= 55 gal, UEF = 3.75, replacing electric storage water heater, 40 gal, UEF = 0.92
>=45 to <=55 | 3.75 | 50 gal | 0.92 | Electric storage | Heat pump water heater, => 45 to <= 55 gal, UEF = 3.75, replacing electric storage water heater, 50 gal, UEF = 0.92
>55 to <=75 | 3.3 | 60 gal | 2.91 | Heat pump | Heat pump water heater, > 55 to <= 75 gal, UEF = 3.30, replacing heat pump water heater, 60 gal, UEF = 2.91
>55 to <=75 | 3.5 | 60 gal | 2.91 | Heat pump | Heat pump water heater, > 55 to <= 75 gal, UEF = 3.50, replacing heat pump water heater, 60 gal, UEF = 2.91
>55 to <=75 | 3.75 | 60 gal | 2.91 | Heat pump | Heat pump water heater, > 55 to <= 75 gal, UEF = 3.75, replacing heat pump water heater, 60 gal, UEF = 2.91

## Sheet1 (hidden)
Measure Label | Average of AStdEUkWh | Average of AStdEUkW | Average of AStdEUtherm | Average of APreEUkWh | Average of APreEUkW | Average of APreEUtherm
NG-WtrHt-SmlStrg-Gas-lte75kBtuh-30G-MD-0p64UEF | -8.5599 | -0.00064643 | 8.0609 | 19.0218 | 0.0023846 | 8.4737
NG-WtrHt-SmlStrg-Gas-lte75kBtuh-40G-MD-0p64UEF | 0 | 0 | 0.3565 | 0 | 0 | 0.38956
NG-WtrHt-SmlStrg-Gas-lte75kBtuh-50G-MD-0p64UEF | 0 | 0 | 0.11282 | 0 | 0 | 0.5365
NG-WtrHt-SmlStrg-Gas-lte75kBtuh-30G-HI-0p68UEF | 0 | 0 | 1.6738 | 0 | 0 | 0.99819
NG-WtrHt-SmlStrg-Gas-lte75kBtuh-40G-HI-0p68UEF | 0 | 0 | 1.4569 | 0 | 0 | 1.7144
NG-WtrHt-SmlStrg-Gas-lte75kBtuh-50G-HI-0p68UEF | 0 | 0 | 1.0659 | 0 | 0 | 1.0288
NG-WtrHt-SmlStrg-Gas-lte75kBtuh-30G-HI-0p78UEF | 0 | 0 | 0.37881 | 0 | 0 | 1.235
NG-WtrHt-SmlStrg-Gas-lte75kBtuh-40G-HI-0p78UEF | -1.0084 | -0.00010871 | 6.1588 | -1.0084 | -0.00010871 | 6.4162
NG-WtrHt-SmlStrg-Gas-lte75kBtuh-50G-HI-0p78UEF | -1.5444 | -0.00016637 | 4.9181 | -1.5444 | -0.00016637 | 4.8812
NG-WtrHt-SmlStrg-Gas-lte75kBtuh-30G-HI-0p88UEF | -1.4431 | -0.0001555 | 3.165 | -1.4431 | -0.0001555 | 4.0225
NG-WtrHt-SmlStrg-Gas-lte75kBtuh-40G-HI-0p88UEF | -1.0743 | -0.00011559 | 5.9719 | -1.0743 | -0.00011559 | 6.2269
NG-WtrHt-SmlStrg-Gas-lte75kBtuh-50G-HI-0p88UEF | -0.79681 | -8.5781e-05 | 5.8419 | -0.79681 | -8.5781e-05 | 5.8037
NG-WtrHt-SmlInst-Gas-lt200kBtuh-lt2G-rep40G-MD-0p87UEF | -0.84062 | -9.0537e-05 | 4.5119 | -0.84062 | -9.0537e-05 | 5.3688
NG-WtrHt-SmlInst-Gas-lt200kBtuh-lt2G-rep40G-HI-0p87UEF | -0.79056 | -8.5188e-05 | 5.5875 | -0.79056 | -8.5188e-05 | 6.0119
NG-WtrHt-SmlInst-Gas-lt200kBtuh-lt2G-rep40G-MD-0p81UEF | -0.601 | -6.4787e-05 | 5.4306 | -0.601 | -6.4787e-05 | 5.3937
NG-WtrHt-SmlInst-Gas-lt200kBtuh-lt2G-rep40G-HI-0p81UEF | -0.76631 | -8.2606e-05 | 3.1044 | -0.76631 | -8.2606e-05 | 3.5275
NG-WtrHt-LrgStrg-Gas-gt75kBtuh-0p90Et | -0.56469 | -6.0869e-05 | 3.5638 | -0.56469 | -6.0869e-05 | 3.5275
NG-WtrHt-LrgStrg-Gas-gt75kBtuh-0p96Et | -0.35837 | -3.8594e-05 | 3.6025 | -0.35837 | -3.8594e-05 | 4.2631
NG-WtrHt-LrgInst-Gas-gte200kBtuh-lt2G-0p84Et | -0.44681 | -4.8119e-05 | 3.9487 | -0.44681 | -4.8119e-05 | 4.6087
NG-WtrHt-LrgInst-Gas-gte200kBtuh-lt2G-0p90Et | -0.13575 | -1.4612e-05 | 1.4312 | -0.13575 | -1.4612e-05 | 2.0913
NG-WtrHt-LrgInst-Gas-gte200kBtuh-lt2G-0p96Et | -0.12237 | -1.3198e-05 | 3.8119 | -0.12237 | -1.3198e-05 | 4.4737
NG-WtrHt-SmlInst-Gas-lt200kBtuh-lt2G-0p84Et | -0.12906 | -1.3906e-05 | 4.5194 | -0.12906 | -1.3906e-05 | 5.18
NG-WtrHt-SmlInst-Gas-lt200kBtuh-lt2G-0p90Et | -0.48144 | -5.1863e-05 | 1.2981 | -0.48144 | -5.1863e-05 | 1.9587
NG-WtrHt-SmlInst-Gas-lt200kBtuh-lt2G-0p96Et | -0.55963 | -6.0275e-05 | 3.6544 | -0.55963 | -6.0275e-05 | 4.3144
NG-WtrHt-LrgBoiler-Gas-gte300kBtuh-0p90Et | -0.42581 | -4.5887e-05 | 4.1056 | -0.42581 | -4.5887e-05 | 4.7663
NG-WtrHt-LrgBoiler-Gas-gte300kBtuh-0p96Et | -0.012631 | -1.3617e-06 | 1.2788 | -0.074281 | -8.0025e-06 | 3.3687
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep30G-3.30UEF-50g | -0.023825 | -2.5688e-06 | 2.3281 | -0.085462 | -9.2144e-06 | 4.4188
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep40G-3.30UEF-50g | -241.5 | -0.0253 | 25.0813 | -241.5 | -0.0253 | 25.3188
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep50G-3.30UEF-50g | -241.5 | -0.0253 | 24.8125 | -241.5 | -0.0253 | 24.9812
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep30G-3.50UEF-50g | -241.5 | -0.0253 | 24.7688 | -241.5 | -0.0253 | 24.7688
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep40G-3.50UEF-50g | -235 | -0.024631 | 25.0813 | -235 | -0.024631 | 25.3188
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep50G-3.50UEF-50g | -235 | -0.024631 | 24.8125 | -235 | -0.024631 | 24.9812
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep30G-3.75UEF-50g | -235 | -0.024631 | 24.7688 | -235 | -0.024631 | 24.7688
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep40G-3.75UEF-50g | -221.6875 | -0.023187 | 25.0813 | -221.6875 | -0.023187 | 25.3188
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep50G-3.75UEF-50g | -221.6875 | -0.023187 | 24.8125 | -221.6875 | -0.023187 | 24.9812
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep60G-3.30UEF-65g | -221.6875 | -0.023187 | 24.7688 | -221.6875 | -0.023187 | 24.7688
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep75G-3.30UEF-80g | -238.5 | -0.025056 | 23.425 | -238.5 | -0.025056 | 24.7063
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep60G-3.50UEF-65g | -237.125 | -0.0249 | 26.0938 | -237.125 | -0.0249 | 24.8062
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep75G-3.50UEF-80g | -232.4375 | -0.024394 | 23.425 | -232.4375 | -0.024394 | 24.7063
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep60G-3.75UEF-65g | -225.875 | -0.023569 | 26.0938 | -225.875 | -0.023569 | 24.8062
NE-WtrHt-FuelSub-SmlStrg-HP-lte6kW-rep75G-3.75UEF-80g | -215.125 | -0.022513 | 23.425 | -215.125 | -0.022513 | 24.7063
NE-WtrHt-SmlStrg-HP-lte6kW-rep30G-3p30UEF-50g | -207.1875 | -0.021675 | 26.0938 | -207.1875 | -0.021675 | 24.8062
NE-WtrHt-SmlStrg-HP-lte6kW-rep40G-3p30UEF-50g | 305.1875 | 0.033594 | 0 | 310.3125 | 0.034112 | 0
NE-WtrHt-SmlStrg-HP-lte6kW-rep50G-3p30UEF-50g | 303.5625 | 0.033406 | 0 | 309.8125 | 0.03405 | 0
NE-WtrHt-SmlStrg-HP-lte6kW-rep30G-3p50UEF-50g | 302.875 | 0.033325 | 0 | 310.125 | 0.034094 | 0
NE-WtrHt-SmlStrg-HP-lte6kW-rep40G-3p50UEF-50g | 311.625 | 0.034275 | 0 | 316.75 | 0.0348 | 0
NE-WtrHt-SmlStrg-HP-lte6kW-rep50G-3p50UEF-50g | 309.6875 | 0.0341 | 0 | 316.125 | 0.034744 | 0
NE-WtrHt-SmlStrg-HP-lte6kW-rep30G-3p75UEF-50g | 309.25 | 0.034019 | 0 | 316.5 | 0.03475 | 0
NE-WtrHt-SmlStrg-HP-lte6kW-rep40G-3p75UEF-50g | 324.9375 | 0.035681 | 0 | 330.0625 | 0.036219 | 0
NE-WtrHt-SmlStrg-HP-lte6kW-rep50G-3p75UEF-50g | 323.1875 | 0.035525 | 0 | 329.5 | 0.036156 | 0
NE-WtrHt-SmlStrg-HP-lte6kW-rep60G-3p30UEF-65g | 322.375 | 0.035437 | 0 | 329.625 | 0.0362 | 0
NE-WtrHt-SmlStrg-HP-lte6kW-rep75G-3p30UEF-80g | 41.8438 | 0.0045312 | 0 | 312.25 | 0.034287 | 0
NE-WtrHt-SmlStrg-HP-lte6kW-rep60G-3p50UEF-65g | 32.4813 | 0.0034038 | 0 | 313.9375 | 0.034431 | 0
NE-WtrHt-SmlStrg-HP-lte6kW-rep75G-3p50UEF-80g | 47.9312 | 0.0051769 | 0 | 318.3125 | 0.034925 | 0
NE-WtrHt-SmlStrg-HP-lte6kW-rep60G-3p75UEF-65g | 43.725 | 0.00474 | 0 | 325.3125 | 0.035781 | 0
NE-WtrHt-SmlStrg-HP-lte6kW-rep75G-3p75UEF-80g | 65.225 | 0.0070625 | 0 | 335.6875 | 0.0368 | 0
NE-WtrHt-FuelSub-LrgStrg-HP-gt6kW-120G-4p30COP | 62.35 | 0.0066344 | 0 | 343.8125 | 0.037681 | 0
NG-WtrHt-SmlInst-Gas-lt200kBtuh-lt2G-rep40G-HI-0p92UEF | -173.1875 | -0.018131 | 23.0938 | -173.1875 | -0.018131 | 23.7312
NG-WtrHt-SmlInst-Gas-lt200kBtuh-lt2G-rep40G-HI-0p96UEF | -0.50475 | -5.4413e-05 | 6.2456 | -0.50475 | -5.4413e-05 | 6.2094
NG-WtrHt-SmlInst-Gas-lt200kBtuh-lt2G-HI-0p87UEF | -0.45763 | -4.9312e-05 | 6.815 | -0.45763 | -4.9312e-05 | 6.7769
NG-WtrHt-SmlInst-Gas-lt200kBtuh-lt2G-HI-0p92UEF | -0.036312 | -3.9144e-06 | 1.8662 | -0.601 | -6.4787e-05 | 5.3937
NG-WtrHt-SmlInst-Gas-lt200kBtuh-lt2G-HI-0p96UEF | 0.05995 | 6.4644e-06 | 2.6825 | -0.50475 | -5.4413e-05 | 6.2094
| 0.10732 | 1.1557e-05 | 3.2519 | -0.45763 | -4.9312e-05 | 6.7769

## Lookups (hidden)
HVAC Lookups | [20 empty] | Heating Lookups
[7 empty] | Equipment | Type | Subcategory | Size Category | Options | Index Name | EER Base | IEER/SEER base | Tier 1 Qualifying EER/EER2 | Tier 1 Qualifying IEER2/SEER2 | Baseline Source |  |  |  |  | EFLH - Heat |  | EFLH - Cool |  | NYS TRM Mapping
| ReplacementType |  | WaterCooledChiller | [17 empty] | Space and/or Building Type | Dover, DE | Wilmington, DE | Dover, DE | Wilmington, DE | Building Type | GPD | kBTU_req | DHW Run Hours | CF DHW
| Early Replacement |  | Centrifugal |  |  |  | Air Conditioners | Air Cooled | Split SEER/EER | <5.4 tons | Electric Resistance (or None) | Air Cooled Split SEER/EER <5.4 tons Electric Resistance (or None) | 11.18 | 13 | 12.5 | 15 | IECC 2018 |  |  |  | Assembly | 1114 | 1150 | 937 | 922 | Assembly | 239 | 6059 | 5885 | 0.63
| End of Life/New Construction |  | Centrifugal with VFD |  |  |  |  | Air Cooled | Split SEER/EER | <5.4 tons | Other | Air Cooled Split SEER/EER <5.4 tons Other | 11.18 | 13 | 12.5 | 15 | IECC 2018 |  |  |  | Education - Community College | 713 | 736 | 713 | 701 | Community College | 1520 | 22191 | 2218 | 0.58
| AC Tune-Up |  | Screw/Scroll |  |  |  |  | Air Cooled | Packaged SEER/EER | <5.4 tons | Electric Resistance (or None) | Air Cooled Packaged SEER/EER <5.4 tons Electric Resistance (or None) | 11.76 | 14 | 12.5 | 15 | IECC 2018 |  |  |  | Education - Primary School | 668 | 689 | 293 | 288 | Elementary School | 250 | 22191 | 2218 | 0.58
|  |  | Reciprocating |  |  |  |  | Air Cooled | Packaged SEER/EER | <5.4 tons | Other | Air Cooled Packaged SEER/EER <5.4 tons Other | 11.76 | 14 | 12.5 | 15 | IECC 2018 |  |  |  | Education - Relocatable Classroom | 647 | 668 | 348 | 342 | Elementary School | 250 | 22191 | 2218 | 0.58
| EfficiencyUnits |  | Screw/Scroll/Reciprocating with VFD |  | Efficiency Rating (SEER or SEER2) |  |  | Air Cooled | Split SEER2/EER2 | <5.4 tons | Electric Resistance (or None) | Air Cooled Split SEER2/EER2 <5.4 tons Electric Resistance (or None) | 11.7 | 12.35 | 12 | 15.2 | Federal 2023 SEER2 Update |  |  |  | Education - Secondary School | 719 | 742 | 337 | 331 | High School | 1520 | 22191 | 2218 | 0.58
| EER/SEER/IEER |  |  |  | SEER/EER |  |  | Air Cooled | Split SEER2/EER2 | <5.4 tons | Other | Air Cooled Split SEER2/EER2 <5.4 tons Other | 10.2856 | 12.35 | 12 | 15.2 | Federal 2023 SEER2 Update |  |  |  | Education - University | 530 | 546 | 787 | 774 | University | 1000 | 22191 | 2218 | 0.58
| kW/ton |  | AirCooledChiller |  | SEER2/EER2 |  |  | Air Cooled | Packaged SEER2/EER2 | <5.4 tons | Electric Resistance (or None) | Air Cooled Packaged SEER2/EER2 <5.4 tons Electric Resistance (or None) | 10.8192 | 13.3 | 11.5 | 15.2 | Federal 2023 SEER2 Update |  |  |  | Grocery | 984 | 1015 | 672 | 662 | Grocery | 172 | 6059 | 5885 | 0.63
|  |  | Centrifugal |  |  |  |  | Air Cooled | Packaged SEER2/EER2 | <5.4 tons | Other | Air Cooled Packaged SEER2/EER2 <5.4 tons Other | 10.8192 | 13.3 | 11.5 | 15.2 | Federal 2023 SEER2 Update |  |  |  | Health/Medical - Hospital | 214 | 221 | 1213 | 1194 | Hospital | 16938 | 6059 | 5885 | 0.63
| CapacityUnits |  | Centrifugal with VFD |  |  |  |  | Air Cooled | Split SEER/EER | ≥5.4 to <11.25 tons | Electric Resistance (or None) | Air Cooled Split SEER/EER ≥5.4 to <11.25 tons Electric Resistance (or None) | 11.2 | 12.8 | 12.2 | 14 | IECC 2018 |  |  |  | Health/Medical - Nursing Home | 932 | 962 | 645 | 634 | Dormitory | 8600 | 6059 | 5885 | 0.63
| tons |  | Screw/Scroll/Reciprocating |  |  |  |  | Air Cooled | Split SEER/EER | ≥5.4 to <11.25 tons | Other | Air Cooled Split SEER/EER ≥5.4 to <11.25 tons Other | 11 | 12.6 | 12 | 13.8 | IECC 2018 |  |  |  | Lodging - Hotel | 2242 | 2313 | 1816 | 1787 | Hotel | 9104 | 6059 | 5885 | 0.63
| Btu/h | [6 empty] | Air Cooled | Packaged SEER/EER | ≥5.4 to <11.25 tons | Electric Resistance (or None) | Air Cooled Packaged SEER/EER ≥5.4 to <11.25 tons Electric Resistance (or None) | 11.2 | 12.8 | 12.2 | 14 | IECC 2018 |  |  |  | Manufacturing – Bio Tech/High Tech | 146 | 151 | 867 | 853 | Light Industrial | 489 | 6059 | 5885 | 0.63
|  |  | RoomAirConditioner |  |  |  |  | Air Cooled | Packaged SEER/EER | ≥5.4 to <11.25 tons | Other | Air Cooled Packaged SEER/EER ≥5.4 to <11.25 tons Other | 11 | 12.6 | 12 | 13.8 | IECC 2018 |  |  |  | Manufacturing – 1 Shift/Light Industrial | 585 | 603 | 456 | 449 | Light Industrial | 489 | 6059 | 5885 | 0.63
| AirCooledChillerTier |  | Without Reverse Cycle With louvered sides |  |  |  |  | Air Cooled | Split SEER/EER | ≥11.25 to <20 tons | Electric Resistance (or None) | Air Cooled Split SEER/EER ≥11.25 to <20 tons Electric Resistance (or None) | 11 | 12.4 | 12.2 | 13.2 | IECC 2018 |  |  |  | Multi-Family (Common Areas) | 256 | 264 | 1509 | 1485 | Multi-family Low Rise | 552 | 6059 | 5885 | 0.63
| Path A |  | Without Reverse Cycle Without louvered sides |  |  |  |  | Air Cooled | Split SEER/EER | ≥11.25 to <20 tons | Other | Air Cooled Split SEER/EER ≥11.25 to <20 tons Other | 10.8 | 12.2 | 12 | 13 | IECC 2018 |  |  |  | Office - Large | 221 | 228 | 727 | 716 | Large Office | 550 | 6059 | 5885 | 0.63
| Path B |  | With Reverse Cycle With louvered sides |  |  |  |  | Air Cooled | Packaged SEER/EER | ≥11.25 to <20 tons | Electric Resistance (or None) | Air Cooled Packaged SEER/EER ≥11.25 to <20 tons Electric Resistance (or None) | 11 | 12.4 | 12.2 | 13.2 | IECC 2018 |  |  |  | Office - Small | 440 | 454 | 629 | 619 | Small Office | 110 | 6059 | 5885 | 0.63
|  |  | With Reverse Cycle Without louvered sides |  |  |  |  | Air Cooled | Packaged SEER/EER | ≥11.25 to <20 tons | Other | Air Cooled Packaged SEER/EER ≥11.25 to <20 tons Other | 10.8 | 12.2 | 12 | 13 | IECC 2018 |  |  |  | Restaurant - Fast-Food | 1226 | 1265 | 724 | 712 | Fast Food Restaurant | 500 | 6059 | 5885 | 0.63
| WaterCooledChillerTier |  | Casement Only |  |  |  |  | Air Cooled | Split SEER/EER | ≥20 to <63.3 tons | Electric Resistance (or None) | Air Cooled Split SEER/EER ≥20 to <63.3 tons Electric Resistance (or None) | 10 | 11.6 | 10.5 | 12.3 | IECC 2018 |  |  |  | Restaurant - Sit-Down | 1131 | 1167 | 762 | 750 | Full Service Restaurant | 2500 | 6059 | 5885 | 0.63
| Path A |  | Casement Slider |  |  |  |  | Air Cooled | Split SEER/EER | ≥20 to <63.3 tons | Other | Air Cooled Split SEER/EER ≥20 to <63.3 tons Other | 9.8 | 11.4 | 10.3 | 12.1 | IECC 2018 |  |  |  | Retail - Multistory Large | 591 | 609 | 880 | 866 | Large Retail | 446 | 6059 | 5885 | 0.63
| Path B | [6 empty] | Air Cooled | Packaged SEER/EER | ≥20 to <63.3 tons | Electric Resistance (or None) | Air Cooled Packaged SEER/EER ≥20 to <63.3 tons Electric Resistance (or None) | 10 | 11.6 | 10.5 | 12.3 | IECC 2018 |  |  |  | Retail - Single-Story Large | 739 | 762 | 904 | 890 | Large Retail | 446 | 6059 | 5885 | 0.63
|  |  | PackagedTerminalAirConditioner |  |  |  |  | Air Cooled | Packaged SEER/EER | ≥20 to <63.3 tons | Other | Air Cooled Packaged SEER/EER ≥20 to <63.3 tons Other | 9.8 | 11.4 | 10.3 | 12.1 | IECC 2018 |  |  |  | Retail - Small | 622 | 642 | 915 | 901 | Small Retail | 27 | 6059 | 5885 | 0.63
| Chiller Control Type |  | Standard Size |  |  |  |  | Air Cooled | Split SEER/EER | ≥63.3 tons | Electric Resistance (or None) | Air Cooled Split SEER/EER ≥63.3 tons Electric Resistance (or None) | 9.7 | 11.2 | 9.9 | 11.6 | IECC 2018 |  |  |  | Storage - Conditioned | 854 | 881 | 243 | 239 | Warehouse | 465 | 6059 | 5885 | 0.63
| VFD |  | Non-Standard Size |  |  |  |  | Air Cooled | Split SEER/EER | ≥63.3 tons | Other | Air Cooled Split SEER/EER ≥63.3 tons Other | 9.5 | 11 | 9.7 | 11.4 | IECC 2018 |  |  |  | Warehouse - Refrigerated | 342 | 353 | 3886 | 3824 | Warehouse | 465 | 6059 | 5885 | 0.63
| Other | [6 empty] | Air Cooled | Packaged SEER/EER | ≥63.3 tons | Electric Resistance (or None) | Air Cooled Packaged SEER/EER ≥63.3 tons Electric Resistance (or None) | 9.7 | 11.2 | 9.9 | 11.6 | IECC 2018 |  |  |  | Mid-Atlantic TRM V9 - Full Load Heating Hours by Location and Building Type, Full Load Cooling Hours by Location and Building Type
|  |  | UnitaryAirConditioner |  |  |  |  | Air Cooled | Packaged SEER/EER | ≥63.3 tons | Other | Air Cooled Packaged SEER/EER ≥63.3 tons Other | 9.5 | 11 | 9.7 | 11.4 | IECC 2018 |  |  |  | https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf
| Economizer Control |  | Split |  |  |  |  | Water Cooled | Split SEER/EER | <5.4 tons | Electric Resistance (or None) | Water Cooled Split SEER/EER <5.4 tons Electric Resistance (or None) | 12.1 | 12.3 | 14 | 0 | IECC 2018 |  |  |  | NYS TRM V8 - GPD
| None |  | Packaged |  |  |  |  | Water Cooled | Split SEER/EER | <5.4 tons | Other | Water Cooled Split SEER/EER <5.4 tons Other | 11.9 | 12.1 | 14 | 0 | IECC 2018 |  |  |  | https://www3.dps.ny.gov/W/PSCWeb.nsf/96f0fec0b45a3c6485257688006a701a/72c23decff52920a85257f1100671bdd/$FILE/NYS%20TRM%20V8.pdf
| Dual Enthalpy Economizer | [6 empty] | Water Cooled | Packaged SEER/EER | <5.4 tons | Electric Resistance (or None) | Water Cooled Packaged SEER/EER <5.4 tons Electric Resistance (or None) | 12.1 | 12.3 | 14 | 0 | IECC 2018 | [11 empty] | DHW Baseline Efficiency
| Other |  | UnitaryHeatPump |  |  |  |  | Water Cooled | Packaged SEER/EER | <5.4 tons | Other | Water Cooled Packaged SEER/EER <5.4 tons Other | 11.9 | 12.1 | 14 | 0 | IECC 2018 |  |  |  | Subcategory | Efficiency | Unit |  |  | Average Outdoor Air Temperature |  |  | Electric Resistance | 0.92
|  |  | Split |  |  |  |  | Water Cooled | Split SEER/EER | ≥5.4 to <11.25 tons | Electric Resistance (or None) | Water Cooled Split SEER/EER ≥5.4 to <11.25 tons Electric Resistance (or None) | 12.1 | 13.9 | 14 | 15.3 | IECC 2018 |  |  |  | <300,000 Btuh/h |  |  |  | Dover | 58.4 | °F |  | Gas Storage | 0.61
| Air Conditioner Types |  | Packaged |  |  |  |  | Water Cooled | Split SEER/EER | ≥5.4 to <11.25 tons | Other | Water Cooled Split SEER/EER ≥5.4 to <11.25 tons Other | 11.9 | 13.7 | 13.8 | 15.1 | IECC 2018 |  |  |  | Steam | 80% | AFUE |  | Wilmington | 54.3 | °F |  | Gas Tankless | 0.81
| Air Cooled | [6 empty] | Water Cooled | Packaged SEER/EER | ≥5.4 to <11.25 tons | Electric Resistance (or None) | Water Cooled Packaged SEER/EER ≥5.4 to <11.25 tons Electric Resistance (or None) | 12.1 | 13.9 | 14 | 15.3 | IECC 2018 |  |  |  | Hot Water | 82% | AFUE |  | https://en.climate-data.org/
| Water Cooled |  | VRFHeatPump |  |  |  |  | Water Cooled | Packaged SEER/EER | ≥5.4 to <11.25 tons | Other | Water Cooled Packaged SEER/EER ≥5.4 to <11.25 tons Other | 11.9 | 13.7 | 13.8 | 15.1 | IECC 2018 |  |  |  | >300,000 and <2,500,000 Btu/h
| Evaporatively Cooled |  | with Heat Recovery |  |  |  |  | Water Cooled | Split SEER/EER | ≥11.25 to <20 tons | Electric Resistance (or None) | Water Cooled Split SEER/EER ≥11.25 to <20 tons Electric Resistance (or None) | 12.5 | 13.9 | 14 | 14.8 | IECC 2018 |  |  |  | Hot Water | 80% | Et
|  |  | without Heat Recovery |  |  |  |  | Water Cooled | Split SEER/EER | ≥11.25 to <20 tons | Other | Water Cooled Split SEER/EER ≥11.25 to <20 tons Other | 12.3 | 13.7 | 13.8 | 14.6 | IECC 2018 |  |  |  | Steam - all, except natural draft | 79% | Et
| Heat Pump Types | [6 empty] | Water Cooled | Packaged SEER/EER | ≥11.25 to <20 tons | Electric Resistance (or None) | Water Cooled Packaged SEER/EER ≥11.25 to <20 tons Electric Resistance (or None) | 12.5 | 13.9 | 14 | 14.8 | IECC 2018 |  |  |  | Steam - natural draft | 77% | Et
| Air Source |  | HeatingType |  |  |  |  | Water Cooled | Packaged SEER/EER | ≥11.25 to <20 tons | Other | Water Cooled Packaged SEER/EER ≥11.25 to <20 tons Other | 12.3 | 13.7 | 13.8 | 14.6 | IECC 2018 |  |  |  | >2,500,000 Btu/h
| Water Source |  | Electric Resistance |  |  |  |  | Water Cooled | Split SEER/EER | ≥20 to <63.3 tons | Electric Resistance (or None) | Water Cooled Split SEER/EER ≥20 to <63.3 tons Electric Resistance (or None) | 12.4 | 13.6 | 14 | 14.8 | IECC 2018 |  |  |  | Hot Water | 82% | Ec
| Ground Source |  | Other |  |  |  |  | Water Cooled | Split SEER/EER | ≥20 to <63.3 tons | Other | Water Cooled Split SEER/EER ≥20 to <63.3 tons Other | 12.2 | 13.4 | 13.8 | 14.6 | IECC 2018 |  |  |  | Steam - all, except natural draft | 79% | Et
|  |  | None |  |  |  |  | Water Cooled | Packaged SEER/EER | ≥20 to <63.3 tons | Electric Resistance (or None) | Water Cooled Packaged SEER/EER ≥20 to <63.3 tons Electric Resistance (or None) | 12.4 | 13.6 | 14 | 14.8 | IECC 2018 |  |  |  | Steam - natural draft | 77% | Et
| Air Source Types | [6 empty] | Water Cooled | Packaged SEER/EER | ≥20 to <63.3 tons | Other | Water Cooled Packaged SEER/EER ≥20 to <63.3 tons Other | 12.2 | 13.4 | 13.8 | 14.6 | IECC 2018 |  |  |  | Mid-Atlantic TRM V9 - Gas Boiler - Time of Sale Baseline Efficiency
| Split |  | Chillers |  |  |  |  | Water Cooled | Split SEER/EER | ≥63.3 tons | Electric Resistance (or None) | Water Cooled Split SEER/EER ≥63.3 tons Electric Resistance (or None) | 12.2 | 13.5 | 14 | 14.8 | IECC 2018
| Packaged |  | Air Cooled |  |  |  |  | Water Cooled | Split SEER/EER | ≥63.3 tons | Other | Water Cooled Split SEER/EER ≥63.3 tons Other | 12 | 13.3 | 13.8 | 14.6 | IECC 2018 |  |  |  | Location | HDD45 | HDD55 | Tdesign | LRF
|  |  | Water Cooled, Positive Displacement |  |  |  |  | Water Cooled | Packaged SEER/EER | ≥63.3 tons | Electric Resistance (or None) | Water Cooled Packaged SEER/EER ≥63.3 tons Electric Resistance (or None) | 12.2 | 13.5 | 14 | 14.8 | IECC 2018 |  |  |  | Wilmington, DE | 840 | 1697 | 11 | 60.75%
| PTAC/PTHP |  | Water Cooled, Centrifugal |  |  |  |  | Water Cooled | Packaged SEER/EER | ≥63.3 tons | Other | Water Cooled Packaged SEER/EER ≥63.3 tons Other | 12 | 13.3 | 13.8 | 14.6 | IECC 2018 |  |  |  | Baltimore, MD | 721 | 1499 | 15 | 60.12%
| Packaged Terminal Air Conditioner | [6 empty] | Evaporatively Cooled | Split SEER/EER | <5.4 tons | Electric Resistance (or None) | Evaporatively Cooled Split SEER/EER <5.4 tons Electric Resistance (or None) | 12.1 | 12.3 | 14 | 0 | IECC 2018 |  |  |  | Washington, DC | 560 | 1325 | 18 | 53.69%
| Packaged Terminal Heat Pump |  | Evaporator Fan Motor |  |  |  |  | Evaporatively Cooled | Split SEER/EER | <5.4 tons | Other | Evaporatively Cooled Split SEER/EER <5.4 tons Other | 11.9 | 12.1 | 14 | 0 | IECC 2018 |  |  |  | Mid-Atlantic TRM V9 - Infrared Heaters - HDD, Tdesign and LRF values for selected cities
|  |  | Shaded Pole (SP) |  |  |  |  | Evaporatively Cooled | Packaged SEER/EER | <5.4 tons | Electric Resistance (or None) | Evaporatively Cooled Packaged SEER/EER <5.4 tons Electric Resistance (or None) | 12.1 | 12.3 | 14 | 0 | IECC 2018
| Connected to Network |  | Permanent Split Capacitor (PST) - Not Eligible |  |  |  |  | Evaporatively Cooled | Packaged SEER/EER | <5.4 tons | Other | Evaporatively Cooled Packaged SEER/EER <5.4 tons Other | 11.9 | 12.1 | 14 | 0 | IECC 2018 |  |  |  | Facility Type | Hours of Pre rinse per day
| No | [6 empty] | Evaporatively Cooled | Split SEER/EER | ≥5.4 to <11.25 tons | Electric Resistance (or None) | Evaporatively Cooled Split SEER/EER ≥5.4 to <11.25 tons Electric Resistance (or None) | 12.1 | 12.3 | 14 | 15.3 | IECC 2018 |  |  |  | Full Service Restaurant | 4
| Yes | [6 empty] | Evaporatively Cooled | Split SEER/EER | ≥5.4 to <11.25 tons | Other | Evaporatively Cooled Split SEER/EER ≥5.4 to <11.25 tons Other | 11.9 | 12.1 | 13.8 | 15.1 | IECC 2018 |  |  |  | Other | 2
[8 empty] | Evaporatively Cooled | Packaged SEER/EER | ≥5.4 to <11.25 tons | Electric Resistance (or None) | Evaporatively Cooled Packaged SEER/EER ≥5.4 to <11.25 tons Electric Resistance (or None) | 12.1 | 12.3 | 14 | 15.3 | IECC 2018 |  |  |  | Limited Service Restaurant | 1
| Equipment | Measure Life | [5 empty] | Evaporatively Cooled | Packaged SEER/EER | ≥5.4 to <11.25 tons | Other | Evaporatively Cooled Packaged SEER/EER ≥5.4 to <11.25 tons Other | 11.9 | 12.1 | 13.8 | 15.1 | IECC 2018 |  |  |  | Mid-Atlantic TRM V9 - Pre-Rinse Spray Valves
| Chillers | 23 | [5 empty] | Evaporatively Cooled | Split SEER/EER | ≥11.25 to <20 tons | Electric Resistance (or None) | Evaporatively Cooled Split SEER/EER ≥11.25 to <20 tons Electric Resistance (or None) | 12 | 12.2 | 13.5 | 14.3 | IECC 2018
| Air Conditioners | 15 | [5 empty] | Evaporatively Cooled | Split SEER/EER | ≥11.25 to <20 tons | Other | Evaporatively Cooled Split SEER/EER ≥11.25 to <20 tons Other | 11.8 | 12 | 13.3 | 14.1 | IECC 2018 |  |  |  | Gas Water Heater
| Air Source Heat Pumps | 15 | [5 empty] | Evaporatively Cooled | Packaged SEER/EER | ≥11.25 to <20 tons | Electric Resistance (or None) | Evaporatively Cooled Packaged SEER/EER ≥11.25 to <20 tons Electric Resistance (or None) | 12 | 12.2 | 13.5 | 14.3 | IECC 2018 |  |  |  | Electric Water Heater
| PTAC/PTHP | 15 | [5 empty] | Evaporatively Cooled | Packaged SEER/EER | ≥11.25 to <20 tons | Other | Evaporatively Cooled Packaged SEER/EER ≥11.25 to <20 tons Other | 11.8 | 12 | 13.3 | 14.1 | IECC 2018
| DMSHP | 18 | [5 empty] | Evaporatively Cooled | Split SEER/EER | ≥20 to <63.3 tons | Electric Resistance (or None) | Evaporatively Cooled Split SEER/EER ≥20 to <63.3 tons Electric Resistance (or None) | 11.9 | 12.1 | 13.5 | 14.3 | IECC 2018 |  |  |  | Control Type | Savings Factor
| VFD | 15 | [5 empty] | Evaporatively Cooled | Split SEER/EER | ≥20 to <63.3 tons | Other | Evaporatively Cooled Split SEER/EER ≥20 to <63.3 tons Other | 11.7 | 11.9 | 13.3 | 14.1 | IECC 2018 |  |  |  | Boiler Reset | 5%
| Dual Enthalpy Economizer | 10 | [5 empty] | Evaporatively Cooled | Packaged SEER/EER | ≥20 to <63.3 tons | Electric Resistance (or None) | Evaporatively Cooled Packaged SEER/EER ≥20 to <63.3 tons Electric Resistance (or None) | 11.9 | 12.1 | 13.5 | 14.3 | IECC 2018 |  |  |  | Boiler Cut-Out | 2.2%
| Smart Thermostat | 7.5 | [5 empty] | Evaporatively Cooled | Packaged SEER/EER | ≥20 to <63.3 tons | Other | Evaporatively Cooled Packaged SEER/EER ≥20 to <63.3 tons Other | 11.7 | 11.9 | 13.3 | 14.1 | IECC 2018 |  |  |  | Boiler Reset and Cut-Out | 7.1%
| Room Air Conditioner | 12 | [5 empty] | Evaporatively Cooled | Split SEER/EER | ≥63.3 tons | Electric Resistance (or None) | Evaporatively Cooled Split SEER/EER ≥63.3 tons Electric Resistance (or None) | 11.7 | 11.9 | 13.5 | 14.3 | IECC 2018 |  |  |  | Mid-Atlantic TRM V9 - Boiler Reset and Cut-Out Controls
| GSHP | 20 | [5 empty] | Evaporatively Cooled | Split SEER/EER | ≥63.3 tons | Other | Evaporatively Cooled Split SEER/EER ≥63.3 tons Other | 11.5 | 11.7 | 13.3 | 14.1 | IECC 2018
| WSHP | 15 | [5 empty] | Evaporatively Cooled | Packaged SEER/EER | ≥63.3 tons | Electric Resistance (or None) | Evaporatively Cooled Packaged SEER/EER ≥63.3 tons Electric Resistance (or None) | 11.7 | 11.9 | 13.5 | 14.3 | IECC 2018 |  |  |  | Condensing Boiler
[8 empty] | Evaporatively Cooled | Packaged SEER/EER | ≥63.3 tons | Other | Evaporatively Cooled Packaged SEER/EER ≥63.3 tons Other | 11.5 | 11.7 | 13.3 | 14.1 | IECC 2018 |  |  |  | Non-Condensing Boiler
| Type | CF PJM | CF Upeak/SSP
| Air Conditioners <135k Btu/h | 0.36 | 0.588 | [17 empty] | Steam System | Average Steam Trap Inlet Pressure | Dia (diameter of orifice, in.) | HOURS | Hfg (Interpolated from Heat of Vaporization Table)
| Air Conditioners >135k Btu/h | 0.567 | 0.874 |  |  |  | Equipment | Type | Subcategory | Size Category | Options | Index Name | EER Base | IEER/SEER Base | HSPF/COP Base | Tier 1 Qualifying EER | Tier 1 Qualifying IEER/SEER | Tier 1 Qualifying COP/HSPF | Baseline Source |  | Medium Pressure (>15 psig, <30psig) | 16 | 0.1875 | 8631 | 944
| Air Source Heat Pumps | 0.36 | 0.588 | [17 empty] | Medium Pressure (≥30 psig, <75 psig) | 47 | 0.25 | 8284 | 914.4
| PTAC/PTHP | 0.36 | 0.588 |  |  |  | Heat Pumps | Air Source | Split SEER/EER | <5.4 tons | Electric Resistance (or None) | Air Source Split SEER/EER <5.4 tons Electric Resistance (or None) | 11.76 | 14 | 8.2 | 12.5 | 15 | 8.5 | IECC 2018 |  | High Pressure (≥75 psig, <125 psig) | 101 | 0.25 | 8100 | 879.52
| Ductless Mini-Splits | 0.36 | 0.588 |  |  |  |  | Air Source | Split SEER/EER | <5.4 tons | Other | Air Source Split SEER/EER <5.4 tons Other | 11.6472 | 13.8 | 8.2 | 12.5 | 15 | 8.5 | IECC 2018 |  | High Pressure (≥125 psig, <175 psig) | 146 | 0.25 | 8346 | 858.76
| Room AC | 0.3 | 0.31 |  |  |  |  | Air Source | Packaged SEER/EER | <5.4 tons | Electric Resistance (or None) | Air Source Packaged SEER/EER <5.4 tons Electric Resistance (or None) | 11.76 | 14 | 8 | 12 | 15 | 8.2 | IECC 2018 |  | High Prssure (≥175 psig, <250 psig) | 202 | 0.25 | 7788 | 836.28
| GSHP/WSHP | 0.66 | 0.69 |  |  |  |  | Air Source | Packaged SEER/EER | <5.4 tons | Other | Air Source Packaged SEER/EER <5.4 tons Other | 11.6472 | 13.8 | 8 | 12 | 15 | 8.2 | IECC 2018 |  | High Pressure (≥250 psig, ≤300 psig) | 263 | 0.25 | 8746 | 815.84
| Chillers | 0.808 | 0.923 |  |  |  |  | Air Source | Split SEER2/EER2 | <5.4 tons | Electric Resistance (or None) | Air Source Split SEER2/EER2 <5.4 tons Electric Resistance (or None) | 10.5 | 15 | 7.5 | 11 | 16 | 8 | Federal 2023 SEER2 Update |  | High Pressure (>300 psig) | Custom | Custom | 8746
| Mid-Atlantic TRM V9 | [6 empty] | Air Source | Split SEER2/EER2 | <5.4 tons | Other | Air Source Split SEER2/EER2 <5.4 tons Other | 10.5 | 15 | 7.5 | 11 | 16 | 8 | Federal 2023 SEER2 Update |  | Mid-Atlantic TRM V9 - Steam Boiler Traps - Repair/Replace
[8 empty] | Air Source | Packaged SEER2/EER2 | <5.4 tons | Electric Resistance (or None) | Air Source Packaged SEER2/EER2 <5.4 tons Electric Resistance (or None) | 10 | 15 | 6.7 | 10 | 15.2 | 7.2 | Federal 2023 SEER2 Update
[8 empty] | Air Source | Packaged SEER2/EER2 | <5.4 tons | Other | Air Source Packaged SEER2/EER2 <5.4 tons Other | 10 | 15 | 6.7 | 10 | 15.2 | 7.2 | Federal 2023 SEER2 Update |  | Pressure (psig) | Heat of Vaporization (Btu/lb)
[8 empty] | Air Source | Split SEER/EER | ≥5.4 to <11.25 tons | Electric Resistance (or None) | Air Source Split SEER/EER ≥5.4 to <11.25 tons Electric Resistance (or None) | 11 | 12 | 3.3 | 11.8 | 13.6 | 3.4 | IECC 2018 |  | 16 | 944
[8 empty] | Air Source | Split SEER/EER | ≥5.4 to <11.25 tons | Other | Air Source Split SEER/EER ≥5.4 to <11.25 tons Other | 10.8 | 11.8 | 3.3 | 11.6 | 13.4 | 3.4 | IECC 2018 |  | 20 | 939
[8 empty] | Air Source | Packaged SEER/EER | ≥5.4 to <11.25 tons | Electric Resistance (or None) | Air Source Packaged SEER/EER ≥5.4 to <11.25 tons Electric Resistance (or None) | 11 | 12 | 3.3 | 11.8 | 13.6 | 3.4 | IECC 2018 |  | 30 | 929
[8 empty] | Air Source | Packaged SEER/EER | ≥5.4 to <11.25 tons | Other | Air Source Packaged SEER/EER ≥5.4 to <11.25 tons Other | 10.8 | 11.8 | 3.3 | 11.6 | 13.4 | 3.4 | IECC 2018 |  | 40 | 920
[8 empty] | Air Source | Split SEER/EER | ≥11.25 to <20 tons | Electric Resistance (or None) | Air Source Split SEER/EER ≥11.25 to <20 tons Electric Resistance (or None) | 10.6 | 11.6 | 3.2 | 10.9 | 12.8 | 3.3 | IECC 2018 |  | 50 | 912
[8 empty] | Air Source | Split SEER/EER | ≥11.25 to <20 tons | Other | Air Source Split SEER/EER ≥11.25 to <20 tons Other | 10.4 | 11.4 | 3.2 | 10.7 | 12.6 | 3.3 | IECC 2018 |  | 60 | 906
[8 empty] | Air Source | Packaged SEER/EER | ≥11.25 to <20 tons | Electric Resistance (or None) | Air Source Packaged SEER/EER ≥11.25 to <20 tons Electric Resistance (or None) | 10.6 | 11.6 | 3.2 | 10.9 | 12.8 | 3.3 | IECC 2018 |  | 75 | 895
[8 empty] | Air Source | Packaged SEER/EER | ≥11.25 to <20 tons | Other | Air Source Packaged SEER/EER ≥11.25 to <20 tons Other | 10.4 | 11.4 | 3.2 | 10.7 | 12.6 | 3.3 | IECC 2018 |  | 100 | 880
[8 empty] | Air Source | Split SEER/EER | ≥20 to <63.3 tons | Electric Resistance (or None) | Air Source Split SEER/EER ≥20 to <63.3 tons Electric Resistance (or None) | 9.5 | 10.6 | 3.2 | 10.3 | 11.8 | 3.3 | IECC 2018 |  | 125 | 868
| EFLH - Heat | [6 empty] | Air Source | Split SEER/EER | ≥20 to <63.3 tons | Other | Air Source Split SEER/EER ≥20 to <63.3 tons Other | 9.3 | 10.4 | 3.2 | 10.1 | 11.6 | 3.3 | IECC 2018 |  | 150 | 857
| Space and/or Building Type | Dover, DE | Wilmington, DE |  |  |  |  | Air Source | Packaged SEER/EER | ≥20 to <63.3 tons | Electric Resistance (or None) | Air Source Packaged SEER/EER ≥20 to <63.3 tons Electric Resistance (or None) | 9.5 | 10.6 | 3.2 | 10.3 | 11.8 | 3.3 | IECC 2018 |  | 175 | 847
| Assembly | 1114 | 1150 |  |  |  |  | Air Source | Packaged SEER/EER | ≥20 to <63.3 tons | Other | Air Source Packaged SEER/EER ≥20 to <63.3 tons Other | 9.3 | 10.4 | 3.2 | 10.1 | 11.6 | 3.3 | IECC 2018 |  | 200 | 837
| Education - Community College | 713 | 736 | [17 empty] | 225 | 828
| Education - Primary School | 668 | 689 |  |  |  |  | Mini-Split | Heat Pump SEER/HSPF | <5.4 tons | N/A | Mini-Split Heat Pump SEER/HSPF <5.4 tons | 11.76 | 14 | 8.2 | 12 | 15 | 8.5 | IECC 2018 - Split ASHP baseline |  | 250 | 820
| Education - Relocatable Classroom | 647 | 668 |  |  |  |  | Mini-Split | Heat Pump SEER2/HSPF2 | <5.4 tons | N/A | Mini-Split Heat Pump SEER2/HSPF2 <5.4 tons | 10 | 14.3 | 7.5 | 11 | 16 | 8 | Federal 2023 SEER2 Update |  | Mid-Atlantic TRM V9 - Steam Boiler Traps - Repair/Replace
| Education - Secondary School | 719 | 742
| Education - University | 530 | 546 | [17 empty] | Yes & No
| Grocery | 984 | 1015 | [17 empty] | (Select yes or no)
| Health/Medical - Hospital | 214 | 221 | [8 empty] | Air Cooled Packaged SEER2/EER2 ≥11.25 to <20 Tons Other | [8 empty] | Yes
| Health/Medical - Nursing Home | 932 | 962 | [17 empty] | No
| Lodging - Hotel | 2242 | 2313
| Manufacturing – Bio Tech/High Tech | 146 | 151 |  |  |  | Equipment | Type | Compliance Path | Size Category | Options | Index Name | Full Load Base | IPLV Base | Tier 1 Qualifying Full Load | Tier 1 Qualifying IPLV | Baseline Source |  |  |  | Organization Type
| Manufacturing – 1 Shift/Light Industrial | 585 | 603 | [17 empty] | (Select one)
| Multi-Family (Common Areas) | 256 | 264 |  |  |  | Chillers | Air Cooled | Path A | <150 tons | N/A | Air Cooled Path A <150 tons | 10.1 | 13.7 | 10.605 | 14.385 | IECC 2018 |  |  |  | Commercial
| Office - Large | 221 | 228 |  |  |  |  | Air Cooled | Path A | ≥150 tons | N/A | Air Cooled Path A ≥150 tons | 10.1 | 14 | 10.605 | 14.7 | IECC 2018 |  |  |  | Industrial
| Office - Small | 440 | 454 |  |  |  |  | Air Cooled | Path B | <150 tons | N/A | Air Cooled Path B <150 tons | 9.7 | 15.8 | 10.185 | 16.59 | IECC 2018 |  |  |  | Tax Exempt Non-Profit
| Restaurant - Fast-Food | 1226 | 1265 |  |  |  |  | Air Cooled | Path B | ≥150 tons | N/A | Air Cooled Path B ≥150 tons | 9.7 | 16.1 | 10.185 | 16.905 | IECC 2018 |  |  |  | Local Government
| Restaurant - Sit-Down | 1131 | 1167 |  |  |  |  | Water Cooled, Positive Displacement | Path A | <75 tons | N/A | Water Cooled, Positive Displacement Path A <75 tons | 0.75 | 0.6 | 0.713 | 0.57 | IECC 2018 |  |  |  | State Agency
| Retail - Multistory Large | 591 | 609 |  |  |  |  | Water Cooled, Positive Displacement | Path A | ≥75 to <150 tons | N/A | Water Cooled, Positive Displacement Path A ≥75 to <150 tons | 0.72 | 0.56 | 0.684 | 0.532 | IECC 2018 |  |  |  | Individual/Sole Proprietor
| Retail - Single-Story Large | 739 | 762 |  |  |  |  | Water Cooled, Positive Displacement | Path A | ≥150 to <300 tons | N/A | Water Cooled, Positive Displacement Path A ≥150 to <300 tons | 0.66 | 0.54 | 0.627 | 0.513 | IECC 2018
| Retail - Small | 622 | 642 |  |  |  |  | Water Cooled, Positive Displacement | Path A | ≥300 to <600 tons | N/A | Water Cooled, Positive Displacement Path A ≥300 to <600 tons | 0.61 | 0.52 | 0.58 | 0.494 | IECC 2018 |  |  |  | Building Heat
| Storage - Conditioned | 854 | 881 |  |  |  |  | Water Cooled, Positive Displacement | Path A | ≥600 tons | N/A | Water Cooled, Positive Displacement Path A ≥600 tons | 0.56 | 0.5 | 0.532 | 0.475 | IECC 2018 |  |  |  | (Select One)
| Warehouse - Refrigerated | 342 | 353 |  |  |  |  | Water Cooled, Positive Displacement | Path B | <75 tons | N/A | Water Cooled, Positive Displacement Path B <75 tons | 0.78 | 0.5 | 0.741 | 0.475 | IECC 2018 |  |  |  | Electric
| Mid-Atlantic TRM V9 - Full Load Heating Hours by Location and Building Type, Full Load Cooling Hours by Location and Building Type | [6 empty] | Water Cooled, Positive Displacement | Path B | ≥75 to <150 tons | N/A | Water Cooled, Positive Displacement Path B ≥75 to <150 tons | 0.75 | 0.49 | 0.713 | 0.466 | IECC 2018 |  |  |  | Steam
[8 empty] | Water Cooled, Positive Displacement | Path B | ≥150 to <300 tons | N/A | Water Cooled, Positive Displacement Path B ≥150 to <300 tons | 0.68 | 0.44 | 0.646 | 0.418 | IECC 2018 |  |  |  | Natural Gas
| EFLH - Cool | [6 empty] | Water Cooled, Positive Displacement | Path B | ≥300 to <600 tons | N/A | Water Cooled, Positive Displacement Path B ≥300 to <600 tons | 0.625 | 0.41 | 0.594 | 0.39 | IECC 2018 |  |  |  | Oil
| Space and/or Building Type | Dover, DE | Wilmington, DE |  |  |  |  | Water Cooled, Positive Displacement | Path B | ≥600 tons | N/A | Water Cooled, Positive Displacement Path B ≥600 tons | 0.585 | 0.38 | 0.556 | 0.361 | IECC 2018 |  |  |  | Other
| Assembly | 937 | 922 |  |  |  |  | Water Cooled, Centrifugal | Path A | <150 tons | N/A | Water Cooled, Centrifugal Path A <150 tons | 0.61 | 0.55 | 0.58 | 0.523 | IECC 2018
| Education - Community College | 713 | 701 |  |  |  |  | Water Cooled, Centrifugal | Path A | ≥150 to <300 tons | N/A | Water Cooled, Centrifugal Path A ≥150 to <300 tons | 0.61 | 0.55 | 0.58 | 0.523 | IECC 2018 |  |  |  | Has ECM
| Education - Primary School | 293 | 288 |  |  |  |  | Water Cooled, Centrifugal | Path A | ≥300 to <400 tons | N/A | Water Cooled, Centrifugal Path A ≥300 to <400 tons | 0.56 | 0.52 | 0.532 | 0.494 | IECC 2018 |  |  |  | Does not have ECM
| Education - Relocatable Classroom | 348 | 342 |  |  |  |  | Water Cooled, Centrifugal | Path A | ≥400 to <600 tons | N/A | Water Cooled, Centrifugal Path A ≥400 to <600 tons | 0.56 | 0.5 | 0.532 | 0.475 | IECC 2018
| Education - Secondary School | 337 | 331 |  |  |  |  | Water Cooled, Centrifugal | Path A | ≥600 tons | N/A | Water Cooled, Centrifugal Path A ≥600 tons | 0.56 | 0.5 | 0.523 | 0.475 | IECC 2018 |  |  |  | Low Intensity
| Education - University | 787 | 774 |  |  |  |  | Water Cooled, Centrifugal | Path B | <150 tons | N/A | Water Cooled, Centrifugal Path B <150 tons | 0.695 | 0.44 | 0.66 | 0.418 | IECC 2018 |  |  |  | High Intensity
| Grocery | 672 | 662 |  |  |  |  | Water Cooled, Centrifugal | Path B | ≥150 to <300 tons | N/A | Water Cooled, Centrifugal Path B ≥150 to <300 tons | 0.635 | 0.4 | 0.603 | 0.38 | IECC 2018
| Health/Medical - Hospital | 1213 | 1194 |  |  |  |  | Water Cooled, Centrifugal | Path B | ≥300 to <400 tons | N/A | Water Cooled, Centrifugal Path B ≥300 to <400 tons | 0.595 | 0.39 | 0.565 | 0.371 | IECC 2018 |  |  |  | °F/hr
| Health/Medical - Nursing Home | 645 | 634 |  |  |  |  | Water Cooled, Centrifugal | Path B | ≥400 to <600 tons | N/A | Water Cooled, Centrifugal Path B ≥400 to <600 tons | 0.585 | 0.38 | 0.556 | 0.361 | IECC 2018 |  |  |  | Btu/h
| Lodging - Hotel | 1816 | 1787 |  |  |  |  | Water Cooled, Centrifugal | Path B | ≥600 tons | N/A | Water Cooled, Centrifugal Path B ≥600 tons | 0.585 | 0.38 | 0.556 | 0.361 | IECC 2018
| Manufacturing – Bio Tech/High Tech | 867 | 853 | [17 empty] | Equipment Type | Efficiency
| Manufacturing – 1 Shift/Light Industrial | 456 | 449 |  |  |  | Equipment | Type | Subcategory | Size Category | Options | Index Name | [8 empty] | Tank Type | 0.8
| Multi-Family (Common Areas) | 1509 | 1485 | [17 empty] | Gas-Fired Hot Water Boiler | 0.82
| Office - Large | 727 | 716 |  |  |  | Smart Thermostat - Heating | Air Source Heat Pump | N/A | <65,000 Btu/h | N/A | Air Source Heat Pump <65,000 Btu/h | [8 empty] | Oil-Fired Hot Water Boiler | 0.84
| Office - Small | 629 | 619 |  |  |  |  | Air Source Heat Pump | N/A | ≥65,000 to <135,000 Btu/h | N/A | Air Source Heat Pump ≥65,000 to <135,000 Btu/h | [8 empty] | Gas-Fired Steam Boiler, All Except Natural Draft | 0.8
| Restaurant - Fast-Food | 724 | 712 |  |  |  |  | Air Source Heat Pump | N/A | ≥135,000 to <240,000 Btu/h | N/A | Air Source Heat Pump ≥135,000 to <240,000 Btu/h | [8 empty] | Gas-Fired Steam Boiler, Natural Draft | 0.8
| Restaurant - Sit-Down | 762 | 750 |  |  |  |  | Air Source Heat Pump | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | Air Source Heat Pump ≥240,000 to ≤300,000 Btu/h | [8 empty] | Oil-Fired Steam Boiler | 0.82
| Retail - Multistory Large | 880 | 866 |  |  |  |  | Electric Resistance | N/A | <65,000 Btu/h | N/A | Electric Resistance <65,000 Btu/h
| Retail - Single-Story Large | 904 | 890 |  |  |  |  | Electric Resistance | N/A | ≥65,000 to <135,000 Btu/h | N/A | Electric Resistance ≥65,000 to <135,000 Btu/h | [8 empty] | Pre-Rinse Sprayer Product Class
| Retail - Small | 915 | 901 |  |  |  |  | Electric Resistance | N/A | ≥135,000 to <240,000 Btu/h | N/A | Electric Resistance ≥135,000 to <240,000 Btu/h | [8 empty] | Product Class 1 (≤ 5.0 ozf) | 1
| Storage - Conditioned | 243 | 239 |  |  |  |  | Electric Resistance | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | Electric Resistance ≥240,000 to ≤300,000 Btu/h | [8 empty] | Product Class 2 (> 5.0 ozf and ≤ 8.0 ozf) | 1.2
| Warehouse - Refrigerated | 3886 | 3824 |  | 0 |  |  | None | N/A | <65,000 Btu/h | N/A | None <65,000 Btu/h | [8 empty] | Product Class 3 (> 8.0 ozf) | 1.28
[8 empty] | None | N/A | ≥65,000 to <135,000 Btu/h | N/A | None ≥65,000 to <135,000 Btu/h
[8 empty] | None | N/A | ≥135,000 to <240,000 Btu/h | N/A | None ≥135,000 to <240,000 Btu/h
| Wilmington | Dover | [5 empty] | None | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | None ≥240,000 to ≤300,000 Btu/h
| New Castle | Kent | [5 empty] | Non-Electric | N/A | <65,000 Btu/h | N/A | Non-Electric <65,000 Btu/h
| 19701 | 19901 | [5 empty] | Non-Electric | N/A | ≥65,000 to <135,000 Btu/h | N/A | Non-Electric ≥65,000 to <135,000 Btu/h
| 19702 | 19902 | [5 empty] | Non-Electric | N/A | ≥135,000 to <240,000 Btu/h | N/A | Non-Electric ≥135,000 to <240,000 Btu/h
| 19703 | 19903 | [5 empty] | Non-Electric | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | Non-Electric ≥240,000 to ≤300,000 Btu/h
| 19706 | 19904 |  |  |  |  | Equipment | Type | Subcategory | Size Category | Options | Index Name
| 19707 | 19905
| 19708 | 19906 |  |  |  |  | Smart Thermostat - Cooling | Air Source Air Conditioner | N/A | <65,000 Btu/h | N/A | Air Source Air Conditioner <65,000 Btu/h
| 19709 | 19934 | [5 empty] | Air Source Air Conditioner | N/A | ≥65,000 to <135,000 Btu/h | N/A | Air Source Air Conditioner ≥65,000 to <135,000 Btu/h
| 19710 | 19936 | [5 empty] | Air Source Air Conditioner | N/A | ≥135,000 to <240,000 Btu/h | N/A | Air Source Air Conditioner ≥135,000 to <240,000 Btu/h
| 19711 | 19938 | [5 empty] | Air Source Air Conditioner | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | Air Source Air Conditioner ≥240,000 to ≤300,000 Btu/h
| 19712 | 19943 | Mid-Atlantic TRM has two locations for determining EFLH. If zip code is in New Castle County, Wilmington will be used. If zip code is in Kent or Sussex, Dover will be used. |  |  |  |  | Water Cooled Air Conditioner | N/A | <65,000 Btu/h | N/A | Water Cooled Air Conditioner <65,000 Btu/h
| 19713 | 19946 | [5 empty] | Water Cooled Air Conditioner | N/A | ≥65,000 to <135,000 Btu/h | N/A | Water Cooled Air Conditioner ≥65,000 to <135,000 Btu/h
| 19714 | 19952 | [5 empty] | Water Cooled Air Conditioner | N/A | ≥135,000 to <240,000 Btu/h | N/A | Water Cooled Air Conditioner ≥135,000 to <240,000 Btu/h
| 19715 | 19953 | [5 empty] | Water Cooled Air Conditioner | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | Water Cooled Air Conditioner ≥240,000 to ≤300,000 Btu/h
| 19716 | 19954 | [5 empty] | Air Source Heat Pump | N/A | <65,000 Btu/h | N/A | Air Source Heat Pump <65,000 Btu/h
| 19717 | 19955 | [5 empty] | Air Source Heat Pump | N/A | ≥65,000 to <135,000 Btu/h | N/A | Air Source Heat Pump ≥65,000 to <135,000 Btu/h
| 19718 | 19961 | [5 empty] | Air Source Heat Pump | N/A | ≥135,000 to <240,000 Btu/h | N/A | Air Source Heat Pump ≥135,000 to <240,000 Btu/h
| 19720 | 19962 | [5 empty] | Air Source Heat Pump | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | Air Source Heat Pump ≥240,000 to ≤300,000 Btu/h
| 19721 | 19964 | [5 empty] | None | N/A | <65,000 Btu/h | N/A | None <65,000 Btu/h
| 19725 | 19977 | [5 empty] | None | N/A | ≥65,000 to <135,000 Btu/h | N/A | None ≥65,000 to <135,000 Btu/h
| 19726 | 19979 | [5 empty] | None | N/A | ≥135,000 to <240,000 Btu/h | N/A | None ≥135,000 to <240,000 Btu/h
| 19730 | 19980 | [5 empty] | None | N/A | ≥240,000 to ≤300,000 Btu/h | N/A | None ≥240,000 to ≤300,000 Btu/h
| 19731 | Sussex
| 19732 | 19930
| 19733 | 19931
| 19734 | 19933
| 19735 | 19939
| 19736 | 19940 | [5 empty] | Dual Enthalpy Economizer - Savings Factors (kWh/ton)
| 19801 | 19941 | [5 empty] | Building Type | Dover, DE | Wilmington, DE
| 19802 | 19944 | [5 empty] | Assembly | 26 | 22
| 19803 | 19945 | [5 empty] | Big Box Retail | 58 | 50
| 19804 | 19947 | [5 empty] | Fast Food | 37 | 32
| 19805 | 19950 | [5 empty] | Full Service Restaurant | 29 | 25
| 19806 | 19951 | [5 empty] | Light Industrial | 24 | 21
| 19807 | 19956 | [5 empty] | Primary School | 40 | 34
| 19808 | 19958 | [5 empty] | Small Office | 58 | 50
| 19809 | 19960 | [5 empty] | Small Retail | 58 | 50
| 19810 | 19963 | [5 empty] | Religious | 6 | 5
| 19850 | 19966 | [5 empty] | Warehouse | 2 | 2
| 19880 | 19967 | [5 empty] | Other | 58 | 50
| 19884 | 19968
| 19885 | 19969
| 19886 | 19970
| 19887 | 19971 | [5 empty] | CO2 Conversions
| 19889 | 19973 | [5 empty] | 0.00061604 | tco2/kWh
| 19890 | 19975 | [5 empty] | 0.0053 | tco2/therm
| 19891 | [6 empty] | 0.053 | tco2/mmbtu
19892
19893
19894
19895
19896
19897
19898
19899
Retrofit
Manually Operated - Photographs required
Programmable Thermostat
Unknown
| Savings Factors | ElecCool Saving % | ElecHeat Saving % | FuelHeat Saving %
| Manually Operated | 5% | 4% | 5%
| Programmable Thermostat | 3% | 2% | 2%
| New Construction | 3% | 2% | 2%
| HVAC Unit Type Controlled | Heating Type
| None | None
| Air Source Heat Pump | Air Source Heat Pump
| Air Source Air Conditioner | Electric Resistance
| Water Cooled Air Conditioner | Non-Electric
Default Fan Duty Cycle
| Flow Fraction (% of Design CFM) |  | % of Time at Flow Fraction (%FF)
| Min | Max
| 0 | 10 | 0%
| 10 | 20 | 1%
| 20 | 30 | 5.5%
| 30 | 40 | 15.5%
| 40 | 50 | 22%
| 50 | 60 | 25%
| 60 | 70 | 19%
| 70 | 80 | 8.5%
| 80 | 90 | 3%
| 90 | 100 | 0.5%
| Source: Mid-Atlantic TRM V9 - p.428 |  |  |  |  | Motor HP | Incentive | Units |  | HVAC Pump VFD Savings Factors | [10 empty] | Σ(%FF * PLR)
[6 empty] | 2 | 500 | Per unit |  | System | ESF | DSF
[6 empty] | 3 | 600 | Per unit |  | Chilled Water Pump | 0.633 | 0.46
| VFD Operating Hours by Application and Building Type (RHRSbase) |  |  |  |  | 4 | 700 | Per unit |  | Hot Water Pump | 0.652 | 0 | [8 empty] | 1
| Facility Type | Fan Motor Hours | Chilled Water Pumps | Heating Pumps |  | 5 | 800 | Per unit |  | Source: Mid-Atlantic TRM V9 - p.433 | [10 empty] | 0.8059
| Auto Related | 4056 | 1878 | 5376 |  | 7.5 | 900 | Per unit | [12 empty] | 0.7808
| Bakery | 2854 | 1445 | 5376 |  | 10 | 1100 | Per unit | [12 empty] | 0.6994
| Banks, Financial Centers | 3748 | 1767 | 5376 |  | 15 | 1350 | Per unit |  | VFD Application | [10 empty] | 0.6361
| Church | 1955 | 1121 | 5376 |  | 20 | 1500 | Per unit |  | Fan | [10 empty] | 0.53675
| College - Cafeteria | 6376 | 2713 | 5376 |  | 25 | 1600 | Per unit |  | Chilled Water Pump | [10 empty] | 0.532
| College - Classes/Administrative | 2586 | 1348 | 5376 |  | 30 | 1800 | Per unit |  | Heating Hot Water Pump | [10 empty] | 0.49955
| College - Dormitory | 3066 | 1521 | 5376 |  | 40 | 2000 | Per unit | [12 empty] | 0.397
| Commercial Condos | 4055 | 1877 | 5376 |  | 50 | 2500 | Per unit |  | Part Load Ratios by Control and Fan Type and Flow Fractions (PLR) | [10 empty] | 0.301
| Convenience Stores | 6376 | 2713 | 5376 |  | 60 | 3000 | Per unit |  | Control Type | Flow Fraction | [9 empty] | 0.2796
| Convention Center | 1954 | 1121 | 5376 |  | 75 | 3750 | Per unit |  |  | 10% | 20% | 30% | 40% | 50% | 60% | 70% | 80% | 90% | 100%
| Court House | 3748 | 1767 | 5376 |  | 100 | 5000 | Per unit |  | % of Time at Flow Fraction (%FF) | 0% | 1% | 5.5% | 15.5% | 22% | 25% | 19% | 8.5% | 3% | 0.5%
| Dining: Bar Lounge/Leisure | 4182 | 1923 | 5376 |  | >100 to <200 | 50 | Per HP |  | No Control or Bypass Damper | bar: Flow Fraction 10% to Flow Fraction 100%
| Dining: Cafeteria/Fast Food | 6456 | 2742 | 5376 | [5 empty] | Discharge Dampers | 0.46 | 0.55 | 0.63 | 0.7 | 0.77 | 0.83 | 0.88 | 0.93 | 0.97 | 1
| Dining: Family | 4182 | 1923 | 5376 | [5 empty] | Outlet Damper, BI & Airfoil Fans | 0.53 | 0.53 | 0.57 | 0.64 | 0.72 | 0.8 | 0.89 | 0.96 | 1.02 | 1.05
| Entertainment | 1952 | 1120 | 5376 | [5 empty] | Inlet Damper Box | 0.56 | 0.6 | 0.62 | 0.64 | 0.66 | 0.69 | 0.74 | 0.81 | 0.92 | 1.07
| Exercise Center | 5836 | 2518 | 5376 | [5 empty] | Inlet Guide Vane, BI & Airfoil Fans | 0.53 | 0.56 | 0.57 | 0.59 | 0.6 | 0.62 | 0.67 | 0.74 | 0.85 | 1
| Fast Food Restaurants | 6376 | 2713 | 5376 | [5 empty] | Inlet Vane Dampers | 0.38 | 0.4 | 0.42 | 0.44 | 0.48 | 0.53 | 0.6 | 0.7 | 0.83 | 0.99
| Fire Station (Unmanned) | 1953 | 1121 | 5376 | [5 empty] | Outlet Damper, FC Fans | 0.22 | 0.26 | 0.3 | 0.37 | 0.45 | 0.54 | 0.65 | 0.77 | 0.91 | 1.06
| Food Stores | 4055 | 1877 | 5376 | [5 empty] | Eddy Current Drives | 0.17 | 0.2 | 0.25 | 0.32 | 0.41 | 0.51 | 0.63 | 0.76 | 0.9 | 1.04
| Gymnasium | 2586 | 1348 | 5376 | [5 empty] | Inlet Guide Vane, FC Fans | 0.21 | 0.22 | 0.23 | 0.26 | 0.31 | 0.39 | 0.49 | 0.63 | 0.81 | 1.04
| Hospitals | 7674 | 3180 | 8760 | [5 empty] | VFD with duct static pressure controls | 0.09 | 0.1 | 0.11 | 0.15 | 0.2 | 0.29 | 0.41 | 0.57 | 0.76 | 1.01
| Hospitals/Health Care | 7666 | 1377 | 8760 | [5 empty] | VFD with Low/No Duct Static Pressure (<1" w.g.) | 0.05 | 0.06 | 0.09 | 0.12 | 0.18 | 0.27 | 0.39 | 0.55 | 0.75 | 1
| Industrial - 1 Shift | 2857 | 1446 | 5376 | [5 empty] | Source: Mid-Atlantic TRM V9 - p.429
| Industrial - 2 Shift | 4730 | 2120 | 5376
| Industrial - 3 Shift | 6631 | 2805 | 5376 | [5 empty] | Calc Name | Flow Fraction 10%: Data Export Name
| Laundromats | 4056 | 1878 | 5376 | [5 empty] | Fan | Flow Fraction 10%: Fan
| Library | 3748 | 1767 | 5376 | [5 empty] | Chilled Water Pump | Flow Fraction 10%: Chilled Water Pump
| Light Manufacturers | 2857 | 1446 | 5376 | [5 empty] | Heating Hot Water Pump | Flow Fraction 10%: Hot Water Pump
| Lodging (Hotels/Motels) | 3064 | 1521 | 5942 | [5 empty] | No Control or Bypass Damper | Flow Fraction 10%: No Control
| Mall Concourse | 4833 | 2157 | 5376 | [5 empty] | Discharge Dampers | Flow Fraction 10%: Discharge Damper
| Manufacturing Facility | 2857 | 1446 | 5376 | [5 empty] | Outlet Damper, BI & Airfoil Fans | Flow Fraction 10%: Outlet Damper or Airfoil Fans
| Medical Offices | 3748 | 1767 | 5376 | [5 empty] | Inlet Damper Box | Flow Fraction 10%: Inlet Damper Box
| Motion Picture Theatre | 1954 | 1121 | 5376 | [5 empty] | Inlet Guide Vane, BI & Airfoil Fans | Flow Fraction 10%: Inlet Guide Vane
| Multi-Family (Common Areas) | 7665 | 3177 | 5376 | [5 empty] | Inlet Vane Dampers | Flow Fraction 10%: Inlet Vane Dampers
| Museum | 3748 | 1767 | 5376 | [5 empty] | Outlet Damper, FC Fans | Flow Fraction 10%: Outlet Damper or FC Fans
| Nursing Homes | 5840 | 2520 | 5428 | [5 empty] | Eddy Current Drives | Flow Fraction 10%: Eddy Current Dri
| Office (General Office Types) | 3748 | 1767 | 3038 | [5 empty] | Inlet Guide Vane, FC Fans | Flow Fraction 10%: Inlet Guide Vane or FC Fans
| Office/Retail | 3748 | 1767 | 3038 | [5 empty] | VFD with duct static pressure controls | Flow Fraction 10%: VFD with duct static pressure controls
| Parking Garages & Lots | 4368 | 1990 | 5376 | [5 empty] | VFD with Low/No Duct Static Pressure (<1" w.g.) | Flow Fraction 10%: VFD with Low/No Duct Static Pressure (<1" w.g.)
| Penitentiary | 5477 | 2389 | 5376
| Performing Arts Theatre | 2586 | 1348 | 5376
| Policy / Fire Stations (24 Hr) | 7665 | 3177 | 5376
| Post Office | 3748 | 1767 | 5376
| Pump Stations | 1949 | 1119 | 5376
| Refrigerated Warehouse | 2602 | 1354 | 0
| Religious Building | 1955 | 1121 | 5376
| Residential (Except Nursing Homes) | 3066 | 1521 | 5376
| Restaurants | 4182 | 1923 | 5376
| Retail | 4057 | 1878 | 2344
| School / University | 2187 | 1205 | 4038
| Schools (Jr./Sr. High) | 2187 | 1205 | 3229
| Schools (Preschool/Elementary) | 2187 | 1205 | 3229
| Schools (Technical/Vocational) | 2187 | 1205 | 3229
| Small Services | 3750 | 1768 | 5376
| Sports Arena | 1954 | 1121 | 5376
| Town Hall | 3748 | 1767 | 5376
| Transportation | 6456 | 2742 | 5376
| Warehouse (Not Refrigerated) | 2602 | 1354 | 5376
| Waste Water Treatment Plant | 6631 | 2805 | 5376
| Workshop | 3750 | 1768 | 5376
Source: Mid-Atlantic TRM V9 - p.431
Note on R8: Collin Smith: Qualifying efficiencies match Estar requirements for CAC units https://www.energystar.gov/sites/default/files/2024-12/ENERGY%20STAR%20Version%206.2%20Central%20Air%20Conditioner%20and%20Heat%20Pump%20Final%20Specification_0.pdf
Note on R9: Collin Smith: Qualifying efficiencies match Estar requirements for CAC units https://www.energystar.gov/sites/default/files/2024-12/ENERGY%20STAR%20Version%206.2%20Central%20Air%20Conditioner%20and%20Heat%20Pump%20Final%20Specification_0.pdf
Note on R10: Collin Smith: Qualifying efficiencies match Estar requirements for CAC units https://www.energystar.gov/sites/default/files/2024-12/ENERGY%20STAR%20Version%206.2%20Central%20Air%20Conditioner%20and%20Heat%20Pump%20Final%20Specification_0.pdf
Note on R11: Collin Smith: Qualifying efficiencies match Estar requirements for CAC units https://www.energystar.gov/sites/default/files/2024-12/ENERGY%20STAR%20Version%206.2%20Central%20Air%20Conditioner%20and%20Heat%20Pump%20Final%20Specification_0.pdf
Note on R70: Collin Smith: Matches EnergyStar requirements 1/1/2025 https://www.energystar.gov/sites/default/files/2024-12/Final%20ASHP%20ENERGY%20STAR%20Most%20Efficient%202025%20Criteria.pdf
Note on AC3: Required annual heating output for DHW per ASHRAE Handbook, HVAC Applications. Assume Office requirements for all except school types

## Air Conditioners
Air Conditioners
Building Type | Location | Line | Project Type | Installed Equipment | [6 empty] | Cooling |  |  |  | Heating | Removed Equipment |  | Cooling |  |  | New Construction Baseline |  |  |  | Savings Factors |  |  | NC or ER Baseline |  | Qualifying Efficiency |  |  | Estimated Savings
|  |  |  | Manufacturer | Model | AHRI Certified Reference Number | Equipment Type* | Subcategory | Efficiency Rating (SEER or SEER2) | Quantity | Nominal Tons | AHRI Rated Capacity (Btu/h) | EER | IEER/SEER | Heating Type | Model # / Equipment Notes | Equipment Age (Years) | AHRI Rated Capacity (Btu/h) | EER | IEER/SEER | Size Category | Name Index | EER | IEER/SEER | EFLH cool | CF PJM | CF Upeak | EER base | IEER/SEER base | EER | IEER/SEER | Flag | ΔkWh cool | ΔkW PJM | ΔkW Upeak | Incentives
0 | 0 | 1 | [33 empty] | 0
0 | 0 | 2 | [33 empty] | 0
0 | 0 | 3 | [33 empty] | 0
0 | 0 | 4 | [33 empty] | 0
0 | 0 | 5 | [33 empty] | 0
0 | 0 | 6 | [33 empty] | 0
0 | 0 | 7 | [33 empty] | 0
0 | 0 | 8 | [33 empty] | 0
0 | 0 | 9 | [33 empty] | 0
0 | 0 | 10 | [33 empty] | 0
|  | Mid-Atlantic TRM V9 - Unitary HVAC Systems - p.406 | [6 empty] | *Note* SEER/EER should only be selected if unit manufactured prior to 1/1/2023
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## Air Source Heat Pumps
Air Source Heat Pumps
Building Type | Location | Line | Project Type | Installed Equipment | [5 empty] | Cooling |  |  |  | Heating |  |  | Removed Equipment |  | Cooling |  |  | Heating |  | New Construction Baseline |  |  |  |  | Savings Factors |  |  |  | NC or ER Baseline |  |  | Qualifying Efficiency |  |  |  | Savings Calcs
|  |  |  | Manufacturer | Model | AHRI Certified Reference Number | Subcategory | Efficiency Rating (SEER or SEER2) | Quantity | Nominal Tons | AHRI Rated Capacity (Btu/h) | EER | IEER(2)/SEER(2) | Heating Type | AHRI Rated Capacity (Btu/h) | HSPF(2)/COP | Model # / Equipment Notes | Equipment Age (Years) | AHRI Rated Capacity (Btu/h) | EER | IEER/SEER | AHRI Rated Capacity (Btu/h) | HSPF/COP | Size Category | Name Index | EER or EER2 | IEER/SEER or IEER2/SEER2 | HSPF/COP or HSPF2/COP | EFLH cool | EFLH heat | CF PJM | CF Upeak | EER base | IEER/SEER base | HSPF/COP Base | EER2 | IEER2/SEER2 | HSPF2/COP | Flag | ΔkWh cool | ΔkWh heat | ΔkWh total | ΔkW PJM | ΔkW Peak | Estimated Incentive ($)
0 | 0 | 1 | [42 empty] | 0
0 | 0 | 2 | [42 empty] | 0
0 | 0 | 3 | [42 empty] | 0
0 | 0 | 4 | [42 empty] | 0
0 | 0 | 5 | [42 empty] | 0
0 | 0 | 6 | [42 empty] | 0
0 | 0 | 7 | [42 empty] | 0
0 | 0 | 8 | [42 empty] | 0
0 | 0 | 9 | [42 empty] | 0
0 | 0 | 10 | [42 empty] | 0
|  | Mid-Atlantic TRM V9 - Unitary HVAC Systems - p.406 | [5 empty] | *Note* SEER/EER should only be selected if unit manufactured prior to 1/1/2023
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## Ductless & VRF Mini Splits
Ductless and VRF Ductless Mini-Split Heat Pumps
Building Type | Location | Line | Project Type | Installed Equipment | [5 empty] | Cooling |  |  |  | Heating |  |  | Removed Equipment |  | Cooling |  |  | Heating |  | New Construction Baseline |  |  |  |  | Savings Factors |  |  |  | NC or ER Baseline |  |  | Qualifying Efficiency |  |  |  | Savings Calcs
|  |  |  | Manufacturer | Model | AHRI Certified Reference Number | Energy Star Certified (Yes or No) | VRF (Yes or No) | Quantity | Nominal Tons | AHRI Rated Capacity (Btu/h) | EER2 | SEER2 | Heating Type | AHRI Rated Capacity (Btu/h) | HSPF2 | Model # / Equipment Notes | Equipment Age (Years) | AHRI Rated Capacity (Btu/h) | EER | SEER | AHRI Rated Capacity (Btu/h) | HSPF | Size Category | Name Index | EER | SEER | HSPF | EFLH cool | EFLH heat | CF PJM | CF Upeak | EER base | SEER base | HSPF base | SEER | HSPF | Flag | VRF Flag | ΔkWh cool | ΔkWh heat | ΔkWh total | ΔMMBtu | ΔkW PJM | ΔkW Peak | Estimated Incentive ($)
0 | 0 | 1 | [43 empty] | 0
0 | 0 | 2 | [43 empty] | 0
0 | 0 | 3 | [43 empty] | 0
0 | 0 | 4 | [43 empty] | 0
0 | 0 | 5 | [43 empty] | 0
0 | 0 | 6 | [43 empty] | 0
0 | 0 | 7 | [43 empty] | 0
0 | 0 | 8 | [43 empty] | 0
0 | 0 | 9 | [43 empty] | 0
0 | 0 | 10 | [43 empty] | 0
Mid-Atlantic TRM V9 - Ductless Mini-Split Heat Pump - p.429
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## PTAC & PTHP
Packaged Terminal Air Conditioners (PTACs) and Heat Pumps (PTHPs)
|  | Line | Project Type | Installed Equipment | [7 empty] | Cooling |  |  | Heating |  |  | Removed Equipment |  | Cooling |  | Heating |  | NC Baseline |  | Savings Factors |  |  |  | NC or ER baseline |  | Qualifying Efficiency |  |  | Savings Calcs
Building Type | Location |  |  | Manufacturer | Model | AHRI Certified Reference Number | Equipment Type | Size Category | Height (in) | Width (in) | Quantity | Nominal Tons | AHRI Rated Capacity (Btu/h) | EER | AHRI Rated Capacity (Btu/h) | COP | Heating Type | Model # / Equipment Notes | Equipment Age (Years) | AHRI Rated Capacity (Btu/h) | EER | AHRI Rated Capacity (Btu/h) | COP | EER | COP | EFLH cool | EFLH heat | CF PJM | CF Upeak | EER base | COP base | EER | COP | Flag | ΔkWh cool | ΔkWh heat | ΔkWh total | ΔkW PJM | ΔkW Peak | Estimated Incentive ($)
0 | 0 | 1 | [37 empty] | 0
0 | 0 | 2 | [37 empty] | 0
0 | 0 | 3 | [37 empty] | 0
0 | 0 | 4 | [37 empty] | 0
0 | 0 | 5 | [37 empty] | 0
0 | 0 | 6 | [37 empty] | 0
0 | 0 | 7 | [37 empty] | 0
0 | 0 | 8 | [37 empty] | 0
0 | 0 | 9 | [37 empty] | 0
0 | 0 | 10 | [37 empty] | 0
Mid-Atlantic TRM V9 - Unitary HVAC Systems - p.406
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## Chillers
Electric Chillers
Building Type | Location | Line | Project Type | Installed Equipment | [5 empty] | Cooling |  |  |  |  | Removed Equipment |  | Cooling |  |  | New Construction Baseline |  |  |  | Savings Factors |  |  | NC or ER Baseline |  | Qualifying Efficiency |  |  |  | Estimated Savings
Building Type | Location |  | Project Type | Manufacturer | Model | AHRI Certified Reference Number | Equipment Type | Compressor Control Type | Quantity | Nominal Tons | AHRI Rated Capacity (Tons) | Compliance Path | Full Load | IPLV | Model # / Equipment Notes | Equipment Age (Years) | AHRI Rated Capacity (Tons) | Full Load | IPLV | Size Category | Name Index | Full Load | IPLV | EFLH | CF PJM | CF SSP | Full Load base | IPLV base | Full Load | IPLV | IPLV Bonus | Flag | ΔkWh | ΔkW PJM | ΔkW Peak | Estimated Incentive ($)
0 | 0 | 1 | [33 empty] | 0
0 | 0 | 2 | [33 empty] | 0
0 | 0 | 3 | [33 empty] | 0
0 | 0 | 4 | [33 empty] | 0
0 | 0 | 5 | [33 empty] | 0
Mid-Atlantic TRM V9 - Electric Chillers - p.435
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## Gas Furnace
Gas Furnace up to 150 MBH
Line | Building Type Lookup for EFLH | EFLH Location | Manufacturer | Model Number | Size (MBH) | # of Products | Electrically Commutated Motor | AFUE (%) | EFLH | Baseline Efficiency | ECM Flag | Incentive Rate | ΔMMBtu | Estimated Rebate
Ex |  |  | Manufacturer | Model Number | 120 | 2 | Has ECM | 95% | 1150 | 80% | 1 | 500 | 54.4737 | 1000
1 | 0 | 0 | [7 empty] | 80% | 0 | 0 | 0 | 0
2 | 0 | 0 | [7 empty] | 80% | 0 | 0 | 0 | 0
3 | 0 | 0 | [7 empty] | 80% | 0 | 0 | 0 | 0
4 | 0 | 0 | [7 empty] | 80% | 0 | 0 | 0 | 0
5 | 0 | 0 | [7 empty] | 80% | 0 | 0 | 0 | 0
6 | 0 | 0 | [7 empty] | 80% | 0 | 0 | 0 | 0
7 | 0 | 0 | [7 empty] | 80% | 0 | 0 | 0 | 0
8 | 0 | 0 | [7 empty] | 80% | 0 | 0 | 0 | 0
Mid-Atlantic TRM V9 - Gas Furnace - p.447
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## Condensing Unit Heater
Condensing Unit Heater up to 300 MBH
Line | Building Type Lookup for EFLH | EFLH Location | Manufacturer | Model Number | Size (MBH) | # of Products | Thermal Efficiency (%) | EFLH | Baseline Efficiency | Rebate | ΔMMBtu | Estimated Rebate
Ex |  |  | Manufacturer | Model Number | 250 | 2 | 92% | 1150 | 0.8 | 750 | 62.4881 | 1500
1 | 0 | 0 | [6 empty] | 80% | 0 | 0 | 0
2 | 0 | 0 | [6 empty] | 80% | 0 | 0 | 0
3 | 0 | 0 | [6 empty] | 80% | 0 | 0 | 0
4 | 0 | 0 | [6 empty] | 80% | 0 | 0 | 0
5 | 0 | 0 | [6 empty] | 80% | 0 | 0 | 0
6 | 0 | 0 | [6 empty] | 80% | 0 | 0 | 0
7 | 0 | 0 | [6 empty] | 80% | 0 | 0 | 0
8 | 0 | 0 | [6 empty] | 80% | 0 | 0 | 0
Wisconsin Focus on Energy 2020 Technical Reference Manual - Unit Heaters, ≥90% Thermal Efficiency - p. 234
https://insights.esource.com/documents/Wisconsin%20-%204.10.2020%20-%202020%20TRM.pdf

## Infrared Heaters
Infrared Heater, all sizes
Line | Building Type Lookup for EFLH | EFLH Location | Manufacturer | Model Number | Size (MBH) | # of Products | Category | LRF (%) | EFLH | Low Intensity Flag | Base Rebate | ΔMMBtu | Estimated Rebate ($)
Ex |  |  | Manufacturer | Model Number | 255 | 1 | Low Intensity | 60.75% | 1150 | 1 | 750 | 115.1006 | 750
1 | 0 | 0 | [5 empty] | 60.75% |  | 0 |  | 0
2 | 0 | 0 | [5 empty] | 60.75% |  | 0 |  | 0
3 | 0 | 0 | [5 empty] | 60.75% |  | 0 |  | 0
4 | 0 | 0 | [5 empty] | 60.75% |  | 0 |  | 0
5 | 0 | 0 | [5 empty] | 60.75% |  | 0 |  | 0
6 | 0 | 0 | [5 empty] | 60.75% |  | 0 |  | 0
7 | 0 | 0 | [5 empty] | 60.75% |  | 0 |  | 0
8 | 0 | 0 | [5 empty] | 60.75% |  | 0 |  | 0
Mid-Atlantic TRM V9 - Infrared Heaters - p.478
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## Gas Boiler
Condensing Boiler up to 300 MBH
Line | Building Type Lookup for EFLH | EFLH Location | Manufacturer | Model Number | Size (MBH) | Subcategory | # of Products | AFUE (%) | EFLH | Baseline Efficiency | Rebate | ΔMMBtu | Estimated Rebate
Ex |  |  | Manufacturer | Model Number | 250 | Steam | 1 | 90% | 1150 | 80% | 1000 | 39.9306 | 1000
1 | 0 | 0 | [8 empty] | 0 | 0 | 0
2 | 0 | 0 | [8 empty] | 0 | 0 | 0
3 | 0 | 0 | [8 empty] | 0 | 0 | 0
4 | 0 | 0 | [8 empty] | 0 | 0 | 0
5 | 0 | 0 | [8 empty] | 0 | 0 | 0
6 | 0 | 0 | [8 empty] | 0 | 0 | 0
7 | 0 | 0 | [8 empty] | 0 | 0 | 0
8 | 0 | 0 | [8 empty] | 0 | 0 | 0
Mid-Atlantic TRM V9 - Gas Boiler - p.443
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## Tankless Water Heater
Tankless Water Heater
Line | Building Type Lookup for EFLH | EFLH Location | Manufacturer | Model Number | Size (MBH) | # of Products | Thermal Efficiency (%) | GPD | T set | T main | T ambient | ΔT main | ΔT ambient | SL Baseline | UA baseline | Et Baseline | Rebate | ΔMMBtu | Estimated Rebate ($)
Ex |  |  | Manufacturer | Model Number | 199 | 1 | 92% | 239 | 140 | 60.3 | 70 | 79.7 | 70 | 1595.9694 | 22.7996 | 80% | 500 | 26.9186 | 500
1 | 0 | 0 | [5 empty] | #N/A | 140 |  | 70 | #VALUE! | 70 | 1347.2194 | 19.246 | 80% | 0 |  | 0
2 | 0 | 0 | [5 empty] | #N/A | 140 |  | 70 | #VALUE! | 70 | 1347.2194 | 19.246 | 80% | 0 |  | 0
3 | 0 | 0 | [5 empty] | #N/A | 140 |  | 70 | #VALUE! | 70 | 1347.2194 | 19.246 | 80% | 0 |  | 0
4 | 0 | 0 | [5 empty] | #N/A | 140 |  | 70 | #VALUE! | 70 | 1347.2194 | 19.246 | 80% | 0 |  | 0
5 | 0 | 0 | [5 empty] | #N/A | 140 |  | 70 | #VALUE! | 70 | 1347.2194 | 19.246 | 80% | 0 |  | 0
6 | 0 | 0 | [5 empty] | #N/A | 140 |  | 70 | #VALUE! | 70 | 1347.2194 | 19.246 | 80% | 0 |  | 0
7 | 0 | 0 | [5 empty] | #N/A | 140 |  | 70 | #VALUE! | 70 | 1347.2194 | 19.246 | 80% | 0 |  | 0
8 | 0 | 0 | [5 empty] | #N/A | 140 |  | 70 | #VALUE! | 70 | 1347.2194 | 19.246 | 80% | 0 |  | 0
NYS TRM V8 - p. 455
https://www3.dps.ny.gov/W/PSCWeb.nsf/96f0fec0b45a3c6485257688006a701a/72c23decff52920a85257f1100671bdd/$FILE/NYS%20TRM%20V8.pdf

## Comm. Heat Pump Water Heater
Commercial Heat Pump Water Heater
Line | Building Type Lookup for EFLH | EFLH Location | Proposed Manufacturer | Proposed Model Number | Existing Equipment Type | Existing Storage Capacity (Gal) | Existing Efficiency (UEF) | Size (MBH) | # of Products | Proposed Efficiency (UEF) | GPD | kBTU_req | T set | T main | T ambient | ΔT main | ΔT ambient | Runhours | SL Baseline | UA baseline | UEF Baseline | Rebate | ΔkW | ΔkWh | ΔMMBtu | Estimated Rebate
Ex |  |  | Manufacturer | Model Number | Electric Resistance |  |  | 199 | 1 | 3.2 | 239 |  | 140 | 60.3 | 70 | 79.7 | 70 |  | 1595.9694 | 22.7996 | 80% | 500 | 0.14322 | 1337.8854 |  | 750
1 | 0 | 0 | [8 empty] | #N/A | #N/A | 140 |  | 70 | #VALUE! | 70 | #N/A | 1347.2194 | 19.246 |  | 0 | 0 | 0 |  | 0
2 | 0 | 0 | [8 empty] | #N/A | #N/A | 140 |  | 70 | #VALUE! | 70 | #N/A | 1347.2194 | 19.246 |  | 0 | 0 | 0 |  | 0
3 | 0 | 0 | [8 empty] | #N/A | #N/A | 140 |  | 70 | #VALUE! | 70 | #N/A | 1347.2194 | 19.246 |  | 0 | 0 | 0 |  | 0
4 | 0 | 0 | [8 empty] | #N/A | #N/A | 140 |  | 70 | #VALUE! | 70 | #N/A | 1347.2194 | 19.246 |  | 0 | 0 | 0 |  | 0
5 | 0 | 0 | [8 empty] | #N/A | #N/A | 140 |  | 70 | #VALUE! | 70 | #N/A | 1347.2194 | 19.246 |  | 0 | 0 | 0 |  | 0
6 | 0 | 0 | [8 empty] | #N/A | #N/A | 140 |  | 70 | #VALUE! | 70 | #N/A | 1347.2194 | 19.246 |  | 0 | 0 | 0 |  | 0
7 | 0 | 0 | [8 empty] | #N/A | #N/A | 140 |  | 70 | #VALUE! | 70 | #N/A | 1347.2194 | 19.246 |  | 0 | 0 | 0 |  | 0
8 | 0 | 0 | [8 empty] | #N/A | #N/A | 140 |  | 70 | #VALUE! | 70 | #N/A | 1347.2194 | 19.246 |  | 0 | 0 | 0 |  | 0
Mid-Atlantic TRM V9 - C&I Heat Pump Water Heater - p.455
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## High Efficiency Indirect
High Efficiency Indirect Water Heater
Line | Building Type Lookup for EFLH | EFLH Location | Manufacturer | Model Number | Size (Gallons) | # of Products | Standby Losses | Standby Losses Units | Equipment Type | Heating Source Output (MBH) | Heating Source Efficiency (%) | GPD | T set | T main | T ambient | ΔT main | ΔT ambient | SL Baseline | UA baseline | UA efficient | Et Baseline | Rebate | ΔMMBtu | Estimated Rebate
Ex |  |  | Manufacturer | Model Number | 70 | 1 | 45% | °F/hr | Gas-Fired Hot Water Boiler | 120 | 92% | 239 | 140 | 60.3 | 70 | 79.7 | 70 | 1070.326 | 15.2904 | 3.7485 | 82% | 400 | 16.6128 | 400
1 | 0 | 0 | [10 empty] | 140 |  | 70 | #VALUE! | 70 | 0 | 0 | 0 |  | 0 |  | 0
2 | 0 | 0 | [10 empty] | 140 |  | 70 | #VALUE! | 70 | 0 | 0 | 0 |  | 0 |  | 0
3 | 0 | 0 | [10 empty] | 140 |  | 70 | #VALUE! | 70 | 0 | 0 | 0 |  | 0 |  | 0
4 | 0 | 0 | [10 empty] | 140 |  | 70 | #VALUE! | 70 | 0 | 0 | 0 |  | 0 |  | 0
5 | 0 | 0 | [10 empty] | 140 |  | 70 | #VALUE! | 70 | 0 | 0 | 0 |  | 0 |  | 0
6 | 0 | 0 | [10 empty] | 140 |  | 70 | #VALUE! | 70 | 0 | 0 | 0 |  | 0 |  | 0
7 | 0 | 0 | [10 empty] | 140 |  | 70 | #VALUE! | 70 | 0 | 0 | 0 |  | 0 |  | 0
8 | 0 | 0 | [10 empty] | 140 |  | 70 | #VALUE! | 70 | 0 | 0 | 0 |  | 0 |  | 0
NYS TRM V8 - p. 447
https://www3.dps.ny.gov/W/PSCWeb.nsf/96f0fec0b45a3c6485257688006a701a/72c23decff52920a85257f1100671bdd/$FILE/NYS%20TRM%20V8.pdf

## Condensing - Stand Alone
Condensing Stand-Alone Water Heater
Line | Building Type Lookup for EFLH | EFLH Location | Manufacturer | Model Number | Size (Gallons) | # of Products | Standby Losses (Btu/h) | Thermal Efficiency (%) | GPD | Thermal Efficiency Baseline (%) | Standby Losses Baseline (Btu/h) | Rebate | ΔMMBtu | Estimated Rebate
Ex |  |  | Manufacturer | Model Number | 250 | 2 | 1100 | 95% | 239 | 80% | 1292 | 500 | 23.9696 | 1000
1 | 0 | 0 | [7 empty] | 80% | 1292 | 0 | 0 | 0
2 | 0 | 0 | [7 empty] | 80% | 1292 | 0 | 0 | 0
3 | 0 | 0 | [7 empty] | 80% | 1292 | 0 | 0 | 0
4 | 0 | 0 | [7 empty] | 80% | 1292 | 0 | 0 | 0
5 | 0 | 0 | [7 empty] | 80% | 1292 | 0 | 0 | 0
6 | 0 | 0 | [7 empty] | 80% | 1292 | 0 | 0 | 0
7 | 0 | 0 | [7 empty] | 80% | 1292 | 0 | 0 | 0
8 | 0 | 0 | [7 empty] | 80% | 1292 | 0 | 0 | 0
Wisconsin Focus On Energy 2020 Technical Reference Manual - p.142
https://www.focusonenergy.com/sites/default/files/Focus_on_Energy_2020_TRM.pdf

## Pre-Rinse Spray Valves (hidden)
High Efficiency Pre-Rinse Spray Valves
Line | Building Type Lookup for EFLH | EFLH Location | Manufacturer | Model Number | Facility Type | Water Heater Type | Product Class by Spray Force (ozf) | Flow Rate (GPM) | # of Products | Baseline Flow Rate (GPM) | HOT % | Energy Content of Heated Water (BTU/gallon/°F) | Hours of Pre-Rinse Spray Valve Use per Day | Temperature Rise through Water Heater (°F) | Water Heater Thermal Efficiency | Electric Water Heater Efficiency | Gas Water Heater Flag | Electric Water Heater Flag | Rebate | ΔMMBtu | ΔkWh | Estimated Rebate
Ex |  |  | Manufacturer | Model Number | Full Service Restaurant | Gas Water Heater | Product Class 2 (> 5.0 ozf and ≤ 8.0 ozf) | 1.05 | 1 | 1.2 | 69% | 8.33 | 4 | 70 | 75% | 97% | 1 | 0 | 25 | 7.049 | 0 | 25
1 | 0 | 0 | [8 empty] | 69% | 8.33 |  | 70 | 75% | 97% | 0 | 0 | #VALUE! | 0 | 0 | #VALUE!
2 | 0 | 0 | [8 empty] | 69% | 8.33 |  | 70 | 75% | 97% | 0 | 0 | #VALUE! | 0 | 0 | #VALUE!
3 | 0 | 0 | [8 empty] | 69% | 8.33 |  | 70 | 75% | 97% | 0 | 0 | #VALUE! | 0 | 0 | #VALUE!
4 | 0 | 0 | [8 empty] | 69% | 8.33 |  | 70 | 75% | 97% | 0 | 0 | #VALUE! | 0 | 0 | #VALUE!
5 | 0 | 0 | [8 empty] | 69% | 8.33 |  | 70 | 75% | 97% | 0 | 0 | #VALUE! | 0 | 0 | #VALUE!
6 | 0 | 0 | [8 empty] | 69% | 8.33 |  | 70 | 75% | 97% | 0 | 0 | #VALUE! | 0 | 0 | #VALUE!
7 | 0 | 0 | [8 empty] | 69% | 8.33 |  | 70 | 75% | 97% | 0 | 0 | #VALUE! | 0 | 0 | #VALUE!
8 | 0 | 0 | [8 empty] | 69% | 8.33 |  | 70 | 75% | 97% | 0 | 0 | #VALUE! | 0 | 0 | #VALUE!
Mid-Atlantic TRM V9 - Pre-Rinse Spray Valves - p.510
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf
Federal Requirements
https://www.epa.gov/watersense/pre-rinse-spray-valves

## Boiler Controls
After Market Boiler Reset Controls
Line | Building Type Lookup for EFLH | EFLH Location | Manufacturer | Model Number | Boiler Type | Boiler Quantity | Boiler Capacity (MBH) | Subcategory | Control Type | Boiler Name Manager | Savings Percentage | EFLH | Boiler Efficiency | Rebate | ΔMMBtu | Estimated Rebate ($)
Ex |  |  | Manufacturer | Model Number | Condensing Boiler | 1 | 250 | Hot Water | Boiler Reset | Condensing_Boiler | 5% | 1150 | 0.82 | 225 | 17.5305 | 225
1 | 0 | 0 | [7 empty] | 0 |  |  |  | 0 | 0 | 0
2 | 0 | 0 | [7 empty] | 0 |  |  |  | 0 | 0 | 0
3 | 0 | 0 | [7 empty] | 0 |  |  |  | 0 | 0 | 0
4 | 0 | 0 | [7 empty] | 0 |  |  |  | 0 | 0 | 0
5 | 0 | 0 | [7 empty] | 0 |  |  |  | 0 | 0 | 0
6 | 0 | 0 | [7 empty] | 0 |  |  |  | 0 | 0 | 0
7 | 0 | 0 | [7 empty] | 0 |  |  |  | 0 | 0 | 0
8 | 0 | 0 | [7 empty] | 0 |  |  |  | 0 | 0 | 0
Mid-Atlantic TRM V9 - Boiler Reset and Cut-Out Controls - p.473
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## Steam Boiler Traps
Steam Traps
Line | Building Type Lookup for EFLH | EFLH Location | Manufacturer | Model Number | Steam System | # of Products | Average Steam Trap Inlet Pressure (psig) | Diameter of Orifice (in) | Hours | Steam Trap Discharge Rate (lb/hr) | Heat of Vaporization | Boiler Thermal Efficency | Rebate | ΔMMBtu | Estimated Rebate
Ex |  |  | Manufacturer | Model Number | Medium Pressure (≥30 psig, <75 psig) | 15 | 47 | 0.25 | 8284 | 46.7377 | 914.4 | 80.7% | 50 | 438.703 | 750
1 | 0 | 0 | [9 empty] | 80.7% | 0 | 0 | 0
2 | 0 | 0 | [9 empty] | 80.7% | 0 | 0 | 0
3 | 0 | 0 | [9 empty] | 80.7% | 0 | 0 | 0
4 | 0 | 0 | [9 empty] | 80.7% | 0 | 0 | 0
5 | 0 | 0 | [9 empty] | 80.7% | 0 | 0 | 0
6 | 0 | 0 | [9 empty] | 80.7% | 0 | 0 | 0
7 | 0 | 0 | [9 empty] | 80.7% | 0 | 0 | 0
8 | 0 | 0 | [9 empty] | 80.7% | 0 | 0 | 0
Mid-Atlantic TRM V9 - Steam Boiler Traps - Repair/Replace - p.473
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## HVAC VFDs
Variable Frequency Drives (VFD) for HVAC
Line | Motor Application | Manufacturer | Model | Building Type | Baseline Fan Control Type | Retrofit Fan Control Type | Motor Quantity | Motor HP | Nameplate Motor Efficiency | RHRS Base | Σ(%FF x PLRbase) | Σ(%FF x PLRret) | PLRbase | PLRret | Energy Savings Factor (ESF) | Demand Savings Factor (DSF) | Motor Application Data Export | Existing Flow Control Data Export | Efficient Flow Control Data Export | Incentive Rate | Energy Savings (kWh) | Peak Demand Savings (kW) | Incentive ($)
1
2
3
4
5
6
7
8
9
10
Mid-Atlantic TRM V9 - Variable Frequency Drive (VFD) for HVAC - p.427
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## Smart Thermostat
Smart Thermostats (< 65,000 BTU/h Only)
Building Type | Location | Line | Existing Thermostat Type | Manufacturer | Model | Smart Thermostat Quantity | Air Conditioning Type | HVAC Unit Cooling Capacity (Btu/h) | SEER | Heating Type | HVAC Unit Heating Capacity (Btu/h) | HSPF | Heating Capacity of Furnace (Btu/h) | AFUE of controlled unit | Cooling Size Category | Cooling Name Index | Heating Size Category | Heating Name Index | EFLHcool | EFLH Heat | Electric Cool Saving % | Energy Savings (kWh) cooling | Elec Heat Saving % | Energy Savings (kWh) heating | Fuel Heat Saving % | MMBtu Savings | Total Energy Savings (kWh/yr) | Estimated Incentive ($)
0 | 0 | 1 | [25 empty] | 0
0 | 0 | 2 | [25 empty] | 0
0 | 0 | 3 | [25 empty] | 0
0 | 0 | 4 | [25 empty] | 0
0 | 0 | 5 | [25 empty] | 0
0 | 0 | 6 | [25 empty] | 0
0 | 0 | 7 | [25 empty] | 0
0 | 0 | 8 | [25 empty] | 0
0 | 0 | 9 | [25 empty] | 0
0 | 0 | 10 | [25 empty] | 0
Mid-Atlantic TRM V9 - Smart Thermostat - p. 457
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## Chiller Tune-Up (hidden)
Chiller Tune-Up
Building Type | Location | Line | Project Type | Installed Equipment | [5 empty] | Cooling |  |  |  |  | Removed Equipment |  | Cooling |  |  | New Construction Baseline |  |  |  | Savings Factors |  |  | NC or ER Baseline |  | Qualifying Efficiency |  |  | Savings Calcs
Building Type | Location |  | Project Type | Manufacturer | Model | AHRI Certified Reference Number | Equipment Type | Compressor Control Type | Quantity | Nominal Tons | AHRI Rated Capacity (Tons) | Compliance Path | Full Load | IPLV | Model # / Equipment Notes | Equipment Age (Years) | AHRI Rated Capacity (Tons) | Full Load | IPLV | Size Category | Name Index | Full Load | IPLV | EFLH | CF PJM | CF SSP | Full Load base | IPLV base | Full Load | IPLV | Flag | ΔkWh | ΔkW PJM | ΔkW SSP | Incentives
0 | 0 | 1 | [32 empty] | 0
Mid-Atlantic TRM V9 - Electric Chillers - p.435
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## Boiler Tune-Up (hidden)
Boiler Tune-Up
Line | Building Type Lookup for EFLH | EFLH Location | Manufacturer | Model Number | Size (MBH) | Subcategory | # of Products | AFUE (%) | EFLH | Baseline Efficiency | Rebate | ΔMMBtu | Estimated Rebate
Ex |  |  | Manufacturer | Model Number | 250 | Steam | 1 | 90% | 1150 | 80% | 1000 | 39.9306 | 1000
1 | 0 | 0 | [8 empty] | 0 | 0 | 0
2 | 0 | 0 | [8 empty] | 0 | 0 | 0
3 | 0 | 0 | [8 empty] | 0 | 0 | 0
4 | 0 | 0 | [8 empty] | 0 | 0 | 0
5 | 0 | 0 | [8 empty] | 0 | 0 | 0
6 | 0 | 0 | [8 empty] | 0 | 0 | 0
7 | 0 | 0 | [8 empty] | 0 | 0 | 0
8 | 0 | 0 | [8 empty] | 0 | 0 | 0
Mid-Atlantic TRM V9 - Gas Boiler - p.443
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## AC Tune-Up < 65k
AC Tune-UP < 65k BTUh
Building Type | Location | Line | Project Type | Installed Equipment | [5 empty] | Cooling |  |  |  |  | Removed Equipment |  | Cooling |  |  | Savings Factors |  |  | Savings Calcs
|  |  |  | Manufacturer | Model | AHRI Certified Reference Number | Equipment Type | Subcategory | Quantity | Nominal Tons | AHRI Rated Capacity (Btu/h) | EER | IEER/SEER Pre Tune-Up | % Improvement** | Model # / Equipment Notes | Equipment Age (Years) | AHRI Rated Capacity (Btu/h) | EER | IEER/SEER | EFLH cool | CF PJM | CF Upeak | ΔkWh cool | ΔkW Peak | Incentives
| 0 | 1
| 0 | 2
| 0 | 3
| 0 | 4
| 0 | 5
| 0 | 6
| 0 | 7
| 0 | 8
| 0 | 9
| 0 | 10
DE TRM 2021 - AC Tune-Up < 65k BTUh - p.405
Note on L3: Units > 65,000 BTUh should go the custom pathway

## Dual Enthalpy Economizer
Dual Enthalpy Economizer
Building Type | Location | Line | Project Type | Installed Equipment |  |  |  |  | Savings Calcs
|  |  |  | Manufacturer | Model | Economizer Quantity | Tons Capacity | Saving Factor Used (kWh/ton) | Estimated ΔkWh Savings | Estimated Incentive ($)
| 0 | 1
| 0 | 2
| 0 | 3
| 0 | 4
| 0 | 5
| 0 | 6
| 0 | 7
| 0 | 8
| 0 | 9
| 0 | 10
DE TRM 2021 - Dual Enthalpy Economizer - p.402

## ECM Evap Fan Motor
ECM Evaporator Case Fan Motor Retrofit
Line | Motor Application | Manufacturer | Model | Building Type | Existing Motor Type | Equipment Type | Motor Quantity | Existing Motor HP | Proposed ECM HP | Proposed ECM kW per HP | Delta % Power, kW | % On Runtime Uncontrolled | Hours Runtime | WHFe | Energy Savings (kWh) | Peak Demand Savings (kW) | Estimated Incentive ($)
1 | [16 empty] | 0
2 | [16 empty] | 0
3 | [16 empty] | 0
4 | [16 empty] | 0
5 | [16 empty] | 0
6 | [16 empty] | 0
7 | [16 empty] | 0
8 | [16 empty] | 0
9 | [16 empty] | 0
10 | [16 empty] | 0
Measure Description
Evaporator fans circulate air in refrigerated spaces by drawing air across the evaporator coil and into the space. Fans are found in both reach-in and walk-in coolers and freezers. Energy and demand savings for this measure are achieved by reducing motor operating power. Additional savings come from refrigeration interactive effects. Because electronically-commutated motors (ECMs) are more efficient and use less power, they introduce less heat into the refrigerated space compared to the baseline motors and result in a reduction in cooling load on the refrigeration system.
Definition of Baseline Condition
In order for this characterization to apply, the baseline condition is assumed to be an evaporator fan powered by a shaded pole (SP) motor that runs 24 hours a day, seven days per week (24/7) with no controls.
Definition of Efficient Condition
In order for this characterization to apply, the efficient equipment is assumed to be an evaporator fan powered by an ECM that runs 24/7 with no controls.
Mid-Atlantic TRM V9 - Evaporator Fan Electronically-Commutated Motor Retrofit - p.497
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## Air Compressor VSD
Variable Speed Drive Screw Air Compressors
Line | Compressor Type | Manufacturer | Model | Compressor Quantity | Existing Compressor HP | Operating Hours | Coincidence Factor | Existing Compressor Factor | Installed Compressor Factor | Energy Savings (kWh) | Peak Demand Savings (kW) | Estimated Incentive ($)
1
2
3
4
5
6
7
8
9
10
Measure Description
This measure relates to the installation of a new high-efficiency oil-flooded, screw air compressor of 100 HP or less with a variable speed drive. This measure applies to time of sale and new construction.
Definition of Baseline Condition
The baseline condition is a modulating with blow down screw compressor. Baseline compressors choke off the inlet air to modulate the compressor output, resulting in inefficient operation.
Definition of Efficient Condition
A 100 HP or less screw compressor with variable speed control on the motor to match output to the load.
Mid-Atlantic TRM V9 - Variable Speed Drive Screw Air Compressors - p.574
https://neep.org/sites/default/files/resources/Mid_Atlantic_TRM_V9_Final_clean_wUpdateSummary%20-%20CT%20FORMAT.pdf

## Version History (hidden)
Version | Date | Notes | Engineer
V1 | 2021-06-04 | Launch | Conor McGrail
V2 | 2021-11-19 | Added heating calculator | Conor McGrail
V3 | 2022-10-01 | Adding additional HVAC measures | Collin Smith